## Settings
Name | Value | Unit | Comment
Casegroup | RfG | -
Run custom cases | FALSE | - | If custom not selected for casegroup. |  | Western Denmark, DK1, CE |  |  | Eastern Denmark, DK2, N
Projectname | Solbakken | - |  | System Voltage POC | 150 kV | 220 kV | 400kV | 132 kV | 220 kV | 400 kV
Pn | 200 | MW
Default P available | 1 | pu | Used to limit the available power due to e.g. reduced irradiance or wind speed | 1 pu | 152 kV | 220 kV | 400kV | 138 kV | 234 kV | 400 kV
Number of Units | 4 | -
PnG3 | 200 | MW | Allowed generation capacity in POC
PnD3 | -100 | MW | Allowed consumption capacity in POC
Unit A type | Generation
Pn Unit A (Generation) | 250 | MW | Nominal power (Generation)
Default P available or SoC Unit A | 1 | pu | Used to limit the available power due to e.g. reduced irradiance or wind speed or state of charge on battery.
Pn Unit A (Consumption) | 0 | MW | Nominal power (Consumption)
Unit B type | Energy Storage
Pn Unit B (Generation) | 100 | MW | Nominal power (Generation)
Default P available or SoC Unit B | 0.5 | pu | Used to limit the available power due to e.g. reduced irradiance or wind speed or state of charge on battery.
Pn Unit B (Consumption) | -100 | MW | Nominal power (Consumption)
Unit C type | Demand
Pn Unit C (Generation) | 0 | MW | Nominal power (Generation)
Default P available or SoC Unit C | 1 | pu | Used to limit the available power due to e.g. reduced irradiance or wind speed or state of charge on battery.
Pn Unit C (Consumption) | -10 | MW | Nominal power (Consumption)
Unit D type | Generation
Pn Unit D (Generation) | 10 | MW | Nominal power (Generation)
Default P available or SoC Unit D | 1 | pu | Used to limit the available power due to e.g. reduced irradiance or wind speed or state of charge on battery.
Pn Unit D (Consumption) | 0 | MW | Nominal power (Consumption)
Uc | 161.9 | kV | Used for easy setup to make sure simulations, start in normal operation voltage and not 1 pu.
Un | 152 | kV | This will be 1pu in simulations and results
Area | DK1
FSM deadband | 0 | Hz | If any
FSM droop | 6 | %
SCR min | 10 | -
SCR tuning | 20 | -
SCR max | 30 | -
Default Q(U) droop | 4 | %
X/R SCR min | 10 | -
X/R SCR tuning | 15 | -
X/R SCR max | 20 | -
Main Transformer Grounded | FALSE | - | Default grounding setting for the Main Transformer
R0 | 0 | ohm | Grounding impedance of the MTB voltage source
X0 | 0 | ohm | Grounding impedance of the MTB voltage source
Default Q mode | Q | - | Qmode signal from MTB is constant. Qref mode == 0, Q(U) mode == 1 and Qpf == 2.
PSCAD Timestep | 10 | µs
PSCAD Initialization time | 3.55 | s | Atleast 1s
PF flat time | 0.15 | s | Atleast 0,1s
PF variable step | TRUE | -
PF enforced sync. | FALSE | -
PF force asymmetrical sim. | FALSE | -
PF enforce P limits in LDF | TRUE | - | Can be neccesary to turn off when QDSL is utilized for initialization.
PF enforce Q limits in LDF | TRUE | - | Can be neccesary to turn off when QDSL is utilized for initialization.

## Area values
| DK1 |  |  | DK2 |  |  |  | Settings lists
Un | <110 kV | 110 kV <= Un < 300 kV | 300 kV <= Un | <110 kV | 110 kV <= Un < 300 kV | 300 kV <= Un | Selected | RfG | TRUE
Power-frequency control | [7 empty] | DCC | FALSE
LFSM-O start (Hz) | 50.2 | 50.2 | 50.2 | 50.5 | 50.5 | 50.5 | 50.2 | Unit
LFSM-O droop (%) | 5 | 5 | 5 | 4 | 4 | 4 | 5 | Co-located
LFSM-U start (Hz) | 49.8 | 49.8 | 49.8 | 49.5 | 49.5 | 49.5 | 49.8 | Custom
LFSM-U droop (%) | 5 | 5 | 5 | 4 | 4 | 4 | 5
FSM deadband (Hz) | 0 | 0 | 0 | 0 | 0 | 0 | 0
FSM droop (%) | 6 | 6 | 6 | 6 | 6 | 6 | 6
FSM provision (%Pn) | 10 | 10 | 10 | 10 | 10 | 10 | 10
30min operation Fmax | 51.5 | 51.5 | 51.5 | 51.5 | 51.5 | 51.5 | 51.5
30min operation Fmin | 47.5 | 47.5 | 47.5 | 47.5 | 47.5 | 47.5 | 47.5
Reactive power capability (base Uc)
UQ Q=0pu Umax | 1.05 | 1.118 | 1.05 | 1.05 | 1.05 | 1.05 | 1.118
UQ Q=0pu Umin | 0.9 | 0.968 | 0.9 | 0.9 | 0.9 | 0.9 | 0.968
UQ Q=+0.33pu Umax | 1.04 | 1.108 | 1.04 | 1.04 | 1.04 | 1.04 | 1.108
UQ Q=+0.33pu Umin | 0.9 | 0.968 | 0.9 | 0.9 | 0.9 | 0.9 | 0.968
UQ Q=-0.33pu Umax | 1.05 | 1.118 | 1.05 | 1.05 | 1.05 | 1.05 | 1.118
UQ Q=-0.33pu Umin | 0.96 | 1.028 | 0.96 | 0.96 | 0.96 | 0.96 | 1.028
Cont. operation Umax | 1.1 | 1.118 | 1.05 | 1.1 | 1.05 | 1.05 | 1.118
Cont. operation Umin | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
60min operation Umax | 1.1 | 1.15 | 1.1 | 1.1 | 1.1 | 1.1 | 1.15
60min operation Umin | 0.9 | 0.85 | 0.85 | 0.9 | 0.9 | 0.9 | 0.85
LVFRT
LVFT start | 0.9 | 0.85 | 0.85 | 0.9 | 0.9 | 0.9 | 0.85
LVFRT stop | 0.9 | 0.85 | 0.85 | 0.9 | 0.9 | 0.9 | 0.85
Ures | 0.15 | 0 | 0 | 0.15 | 0 | 0 | 0
tclear | 0.25 | 0.15 | 0.15 | 0.25 | 0.15 | 0.15 | 0.15
Uclear | 0.15 | 0 | 0 | 0.15 | 0 | 0 | 0
trec1 | 0.25 | 0.15 | 0.15 | 0.25 | 0.15 | 0.15 | 0.15
Urec1 | 0.15 | 0 | 0 | 0.15 | 0 | 0 | 0
trec2 | 0.25 | 0.15 | 0.15 | 0.25 | 0.15 | 0.15 | 0.15
Urec2 | 0.9 | 0.85 | 0.85 | 0.9 | 0.9 | 0.9 | 0.85
trec3 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
OVRT
U1 | 1.2 | 1.3 | 1.3 | 1.2 | 1.3 | 1.3 | 1.3
t1 | 5 | 0.1 | 0.1 | 5 | 0.1 | 0.1 | 0.1
U2 | 1.15 | 1.2 | 1.2 | 1.15 | 1.2 | 1.2 | 1.2
t2 | 60 | 30 | 30 | 60 | 30 | 30 | 30

## RfG cases
Case |  |  |  | Initial Settings | [10 empty] | Event 1 |  |  |  | Event 2 |  |  |  | Event 3 |  |  |  | Event 4 |  |  |  | Event 5 |  |  |  | Event 6 |  |  |  | Event 7 |  |  |  | Event 8 |  |  |  | Event 9 |  |  |  | Event 10 |  |  |  | Event 11 |  |  |  | Event 12 |  |  |  | Event 13
Rank | RMS | EMT | Name | U0 | P0 | Pavail0 | Pmode | Qmode | Qref0 | QUdroop0 | SCR0 | XR0 | MtrfrGnd0 | Simulationtime | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2
1 | TRUE | TRUE | RfG_SS_flatrun_Q1 | 1.0651 | 0 | Default | LFSM | Q | 0 | Default | 10 | 10 | Default | 60 | PF disconnect all ref.
2 | TRUE | TRUE | RfG_SS_flatrun_Q2 | 1.0651 | 0.5 | Default | LFSM | Q | 0.2 | Default | 10 | 10 | Default | 60 | PF disconnect all ref.
3 | TRUE | TRUE | RfG_SS_flatrun_Q3 | 1.0651 | 0.5 | Default | LFSM | Q | -0.2 | Default | 10 | 10 | Default | 60 | PF disconnect all ref.
4 | TRUE | TRUE | RfG_SS_flatrun_Q4 | 1.0651 | 1 | Default | LFSM | Q | 0.33 | Default | 10 | 10 | Default | 60 | PF disconnect all ref.
5 | TRUE | TRUE | RfG_SS_flatrun_Q5 | 1.0651 | 1 | Default | LFSM | Q | -0.33 | Default | 10 | 10 | Default | 60 | PF disconnect all ref.
6 | TRUE | TRUE | RfG_SS_flatrun_Q6 | 1.0651 | 1 | Default | LFSM | Q | 0 | Default | 10 | 10 | Default | 60 | PF disconnect all ref.
7 | TRUE | TRUE | RfG_SS_flatrun_Uctrl_min | 0.968 | 0.7 | Default | LFSM | Q(U) | 1.0651 | Default | -1 | 0 | Default | 60 | PF disconnect all ref.
8 | TRUE | TRUE | RfG_SS_flatrun_Uctrl_max | 1.118 | 0.7 | Default | LFSM | Q(U) | 1.0651 | Default | -1 | 0 | Default | 60 | PF disconnect all ref.
9 | TRUE | TRUE | RfG_SS_flatrun_PFctrl1 | 1.0651 | 0.7 | Default | LFSM | PF | 0.949 | Default | 10 | 10 | Default | 60 | PF disconnect all ref.
10 | TRUE | TRUE | RfG_SS_flatrun_PFctrl2 | 1.0651 | 0.7 | Default | LFSM | PF | -0.949 | Default | 10 | 10 | Default | 60 | PF disconnect all ref.
11 | TRUE | TRUE | RfG_P_step_up_0.0_0.5 | 1.0651 | 0 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 155 | Pref | 0 | 0.5 | 0
12 | TRUE | TRUE | RfG_P_step_up_0.5_0.7 | 1.0651 | 0.5 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 80 | Pref | 0 | 0.7 | 0
13 | TRUE | TRUE | RfG_P_step_up_0.7_1.0 | 1.0651 | 0.7 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 100 | Pref | 0 | 1 | 0
14 | TRUE | TRUE | RfG_P_step_down_1.0_0.7 | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 100 | Pref | 0 | 0.7 | 0
15 | TRUE | TRUE | RfG_P_step_down_0.7_0.5 | 1.0651 | 0.7 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 80 | Pref | 0 | 0.5 | 0
16 | TRUE | TRUE | RfG_P_step_down_0.5_0.0 | 1.0651 | 0.5 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 155 | Pref | 0 | 0 | 0
17 | TRUE | TRUE | RfG_FSM_step1 | 1.0651 | 0.7 | Default | LFSM+FSM | Default | 0 | Default | 10 | 10 | Default | 60 | Frequency | 0 | 50.199 |  | Frequency | 15 | 50 |  | Frequency | 30 | 49.801 |  | Frequency | 45 | 50
18 | TRUE | TRUE | RfG_FSM_step2 | 1.0651 | 0.7 | Default | LFSM+FSM | Default | 0 | Default | 10 | 10 | Default | 60 | Frequency | 0 | 50.15 |  | Frequency | 15 | 50 |  | Frequency | 30 | 49.85 |  | Frequency | 45 | 50
19 | TRUE | TRUE | RfG_LFSM-OU_step1 | 1.0651 | 0.7 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 100 | Frequency | 0 | 51.5 |  | Frequency | 20 | 50 |  | Frequency | 40 | 48.5 |  | Frequency | 60 | 47.5 |  | Frequency | 80 | 50
20 | TRUE | TRUE | RfG_LFSM-O_ramp | 1.0651 | 0.7 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 21.5 | Frequency | 0 |  | 0.5 | Frequency | 3 | 51.5 | 0 | Frequency | 5 |  | -0.2 | Frequency | 11.5 | 50.2 | 0
21 | TRUE | TRUE | RfG_LFSM-U_ramp | 1.0651 | 0.7 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 21.5 | Frequency | 0 |  | -0.5 | Frequency | 3 | 48.5 | 0 | Frequency | 5 |  | 0.2 | Frequency | 11.5 | 49.8 | 0
22 | TRUE | TRUE | RfG_FSM_LFSM-O_ramp | 1.0651 | 0.7 | Default | LFSM+FSM | Default | 0 | Default | 10 | 10 | Default | 26.5 | Frequency | 0 |  | 0.2 | Frequency | 7.5 | 51.5 | 0 | Frequency | 9 |  | -0.2 | Frequency | 16.5 | 50 | 0
23 | TRUE | TRUE | RfG_FSM_LFSM-U_ramp | 1.0651 | 0.7 | Default | LFSM+FSM | Default | 0 | Default | 10 | 10 | Default | 26.5 | Frequency | 0 |  | -0.2 | Frequency | 7.5 | 48.5 | 0 | Frequency | 9 |  | 0.2 | Frequency | 16.5 | 50 | 0
24 | TRUE | TRUE | RfG_FSM_LFSM-O_step | 1.0651 | 0.7 | Default | LFSM+FSM | Default | 0 | Default | 10 | 10 | Default | 45 | Frequency | 0 | 50.2 |  | Frequency | 5 | 50.5 |  | Frequency | 10 | 50.2 |  | Frequency | 15 | 50.15 |  | Frequency | 25 | 50.5 |  | Frequency | 35 | 50
25 | TRUE | TRUE | RfG_FSM_LFSM-U_step | 1.0651 | 0.7 | Default | LFSM+FSM | Default | 0 | Default | 10 | 10 | Default | 45 | Frequency | 0 | 49.8 |  | Frequency | 5 | 49.5 |  | Frequency | 10 | 49.8 |  | Frequency | 15 | 49.85 |  | Frequency | 25 | 49.5 |  | Frequency | 35 | 50
26 | TRUE | TRUE | RfG_LFSM-O_Pavail | 1.0651 | 1 | 0.5 | LFSM | Default | 0 | Default | 10 | 10 | Default | 50 | Frequency | 10 | 51 |  | Frequency | 30 | 50
27 | TRUE | TRUE | RfG_LFSM-U_Pavail | 1.0651 | 0.5 | 0.7 | LFSM | Default | 0 | Default | 10 | 10 | Default | 30 | Frequency | 5 | 48.5 |  | Frequency | 20 | 50
28 | TRUE | TRUE | RfG_U-Q/Pn_Neutral | 1.0651 | 1 | Default | LFSM | Q | 0 | Default | -1 | 0 | Default | 100 | Voltage | 0 | 1.118 |  | Voltage | 20 | 1.0651 |  | Voltage | 40 | 0.968 |  | Voltage | 80 | 1.0651
29 | TRUE | TRUE | RfG_U-Q/Pn_Neutral_stab | 1.0651 | 1 | Default | LFSM | Q | 0 | Default | 10 | 10 | Default | 100 | dVoltage | 0 | 0.052868 |  | dVoltage | 20 | 0 |  | dVoltage | 40 | -0.097132 |  | dVoltage | 80 | 0
30 | TRUE | TRUE | RfG_U-Q/Pn_underEX | 1.0651 | 1 | Default | LFSM | Q | -0.33 | Default | -1 | 0 | Default | 100 | Voltage | 0 | 1.118 |  | Voltage | 20 | 1.0651 |  | Voltage | 40 | 1.028 |  | Voltage | 80 | 1.0651
31 | TRUE | TRUE | RfG_U-Q/Pn_overEX | 1.0651 | 1 | Default | LFSM | Q | 0.33 | Default | -1 | 0 | Default | 100 | Voltage | 0 | 1.108 |  | Voltage | 20 | 1.0651 |  | Voltage | 40 | 0.968 |  | Voltage | 80 | 1.0651
32 | TRUE | TRUE | RfG_PQ/Pn_Neutral1 | 1.0651 | 1 | Default | LFSM | Q | 0 | Default | 10 | 10 | Default | 155 | Pref | 0 | 0.5 | 0
33 | TRUE | TRUE | RfG_PQ/Pn_Neutral2 | 1.0651 | 0.5 | Default | LFSM | Q | 0 | Default | 10 | 10 | Default | 155 | Pref | 0 | 0 | 0
34 | TRUE | TRUE | RfG_PQ/Pn_underEX1 | 1.0651 | 1 | Default | LFSM | Q | -0.33 | Default | 10 | 10 | Default | 155 | Pref | 0 | 0.5 | 0
35 | TRUE | TRUE | RfG_PQ/Pn_underEX2 | 1.0651 | 0.5 | Default | LFSM | Q | -0.33 | Default | 10 | 10 | Default | 155 | Pref | 0 | 0 | 0
36 | TRUE | TRUE | RfG_PQ/Pn_overEX1 | 1.0651 | 1 | Default | LFSM | Q | 0.33 | Default | 10 | 10 | Default | 155 | Pref | 0 | 0.5 | 0
37 | TRUE | TRUE | RfG_PQ/Pn_overEX2 | 1.0651 | 0.5 | Default | LFSM | Q | 0.33 | Default | 10 | 10 | Default | 155 | Pref | 0 | 0 | 0
38 | TRUE | TRUE | RfG_Ucontrol_Scmin | 1.0651 | 1 | Default | LFSM | Q(U) | 1.0651 | Default | 10 | 10 | Default | 85 | dVoltage | 0 | 0.021303 |  | dVoltage | 7 | 0 |  | dVoltage | 14 | -0.021303 |  | dVoltage | 21 | 0 |  | dVoltage | 28 | 0.042605 |  | dVoltage | 35 | 0 |  | dVoltage | 42 | -0.042605 |  | dVoltage | 49 | 0 |  | dVoltage | 56 | 0.052868 |  | dVoltage | 63 | 0 |  | dVoltage | 70 | -0.097132 |  | dVoltage | 77 | 0
39 | TRUE | TRUE | RfG_Ucontrol_Sctune | 1.0651 | 1 | Default | LFSM | Q(U) | 1.0651 | Default | 20 | 15 | Default | 85 | dVoltage | 0 | 0.021303 |  | dVoltage | 7 | 0 |  | dVoltage | 14 | -0.021303 |  | dVoltage | 21 | 0 |  | dVoltage | 28 | 0.042605 |  | dVoltage | 35 | 0 |  | dVoltage | 42 | -0.042605 |  | dVoltage | 49 | 0 |  | dVoltage | 56 | 0.052868 |  | dVoltage | 63 | 0 |  | dVoltage | 70 | -0.097132 |  | dVoltage | 77 | 0
40 | TRUE | TRUE | RfG_Ucontrol_Scmax | 1.0651 | 1 | Default | LFSM | Q(U) | 1.0651 | Default | 30 | 20 | Default | 85 | dVoltage | 0 | 0.021303 |  | dVoltage | 7 | 0 |  | dVoltage | 14 | -0.021303 |  | dVoltage | 21 | 0 |  | dVoltage | 28 | 0.042605 |  | dVoltage | 35 | 0 |  | dVoltage | 42 | -0.042605 |  | dVoltage | 49 | 0 |  | dVoltage | 56 | 0.052868 |  | dVoltage | 63 | 0 |  | dVoltage | 70 | -0.097132 |  | dVoltage | 77 | 0
41 | TRUE | TRUE | RfG_Ucontrol_FRTsensitivity | 1 | 1 | Default | LFSM | Q(U) | 1 | Default | -1 | 0 | Default | 85 | Voltage | 2 | 0.85 |  | Voltage | 8 | 1 |  | Voltage | 20 | 0.84 |  | Voltage | 26 | 1 |  | Voltage | 40 | 0.86 |  | Voltage | 46 | 0.75 |  | Voltage | 51 | 1 |  | Voltage | 65 | 0.86 |  | Voltage | 71 | 0.65 |  | Voltage | 73 | 1
42 | TRUE | TRUE | RfG_Ucontrol_FRTsensitivity-ramp | 1 | 1 | Default | LFSM | Q(U) | 1 | Default | -1 | 0 | Default | 20 | dVoltage | 2 |  | -0.05 | dVoltage | 6 | -0.2 | 0 | dVoltage | 11 |  | 0.1 | dVoltage | 13 | 0 | 0
43 | TRUE | TRUE | RfG_Uarea_Qreq_1(up) | 1.0651 | 1 | Default | LFSM | Q | 0 | Default | -1 | 0 | Default | 50 | Voltage | 0 | 1.118
44 | TRUE | TRUE | RfG_Uarea_Qreq_2(up) | 1.118 | 1 | Default | LFSM | Q | 0 | Default | -1 | 0 | Default | 50 | Voltage | 0 | 1.15
45 | TRUE | TRUE | RfG_Uarea_Qreq_1(down) | 1.0651 | 1 | Default | LFSM | Q | 0 | Default | -1 | 0 | Default | 50 | Voltage | 0 | 0.968
46 | TRUE | TRUE | RfG_Uarea_Qreq_2(down) | 0.968 | 1 | Default | LFSM | Q | 0 | Default | -1 | 0 | Default | 50 | Voltage | 0 | 0.9
47 | TRUE | TRUE | RfG_Uarea_Qreq_3(down) | 0.9 | 1 | Default | LFSM | Q | 0 | Default | -1 | 0 | Default | 50 | Voltage | 0 | 0.85
48 | TRUE | TRUE | RfG_Uarea_Q(U)req_1(up) | 1.0651 | 1 | Default | LFSM | Q(U) | 1.0651 | Default | -1 | 0 | Default | 50 | Voltage | 0 | 1.118
49 | TRUE | TRUE | RfG_Uarea_Q(U)req_2(up) | 1.118 | 1 | Default | LFSM | Q(U) | 1.0651 | Default | -1 | 0 | Default | 50 | Voltage | 0 | 1.15
50 | TRUE | TRUE | RfG_Uarea_Q(U)req_1(down) | 1.0651 | 1 | Default | LFSM | Q(U) | 1.0651 | Default | -1 | 0 | Default | 50 | Voltage | 0 | 0.968
51 | TRUE | TRUE | RfG_Uarea_Q(U)req_2(down) | 0.968 | 1 | Default | LFSM | Q(U) | 1.0651 | Default | -1 | 0 | Default | 50 | Voltage | 0 | 0.9
52 | TRUE | TRUE | RfG_Uarea_Q(U)req_3(down) | 0.9 | 1 | Default | LFSM | Q(U) | 1.0651 | Default | -1 | 0 | Default | 50 | Voltage | 0 | 0.85
53 | TRUE | TRUE | RfG_Q_control_up | 1.0651 | 1 | Default | LFSM | Q | 0 | Default | 10 | 10 | Default | 120 | Qref | 0 | 0.1 |  | Qref | 30 | 0.2 |  | Qref | 60 | 0.33 |  | Qref | 90 | 0
54 | TRUE | TRUE | RfG_Q_control_down | 1.0651 | 1 | Default | LFSM | Q | 0 | Default | 10 | 10 | Default | 120 | Qref | 0 | -0.1 |  | Qref | 30 | -0.2 |  | Qref | 60 | -0.33 |  | Qref | 90 | 0
55 | TRUE | TRUE | RfG_Qpf_PFref-change | 1.0651 | 1 | Default | LFSM | PF | 1 | Default | 10 | 10 | Default | 120 | Qref | 0 | 0.95 |  | Qref | 30 | 1 |  | Qref | 60 | -0.95 |  | Qref | 90 | 1
56 | TRUE | TRUE | RfG_Qpf_Pref-change | 1.0651 | 0.3 | Default | LFSM | PF | 0.99 | Default | 10 | 10 | Default | 135 | Pref | 0 | 0.4 |  | Pref | 35 | 0.5 |  | Pref | 70 | 0.6 |  | Pref | 100 | 0.7
57 | TRUE | TRUE | RfG_SystemProtect_Q | 1.0651 | 1 | Default | LFSM | Q | 0 | Default | 10 | 10 | Default | 45 | Signal 1 | -1 | 0 |  | Signal 3 | 0 | 1 |  | Signal 1 | 1 | 2 |  | Signal 1 | 15 | 4 |  | Signal 1 | 30 | 0
58 | TRUE | TRUE | RfG_SystemProtect_QU | 1.0651 | 1 | Default | LFSM | Q(U) | 1.0651 | Default | 10 | 10 | Default | 45 | Signal 1 | -1 | 0 |  | Signal 3 | 0 | 1 |  | Signal 1 | 1 | 2 |  | Signal 1 | 15 | 4 |  | Signal 1 | 30 | 0
59 | TRUE | TRUE | RfG_SystemProtect+fault | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 45 | Signal 1 | -1 | 0 |  | Signal 3 | 0 | 1 |  | 3p fault | 1 | 20% | 0.45 | Signal 1 | 1.65 | 4 |  | Signal 1 | 30 | 0
60 | TRUE | TRUE | RfG_MaxPhaseJump1 | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 20 | Phase | 0 | 20 |  | Phase | 2.5 | 0 |  | Phase | 5 | -20 |  | Phase | 7.5 | 0
61 | TRUE | TRUE | RfG_MaxPhaseJump2 | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 20 | Phase | 0 | 6.5 |  | Phase | 0.02 | 13.25 |  | Phase | 0.04 | 20 |  | Phase | 2.5 | 13.5 |  | Phase | 2.52 | 6.75 |  | Phase | 2.54 | 0
62 | TRUE | TRUE | RfG_MaxRoCoF1 | 1.0651 | 0.7 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 20 | Frequency | 0 | 50 | 2 | Frequency | 0.5 |  | -2 | Frequency | 1 |  | 0 | Frequency | 2 | 50 | -0.5 | Frequency | 4 |  | 0.5 | Frequency | 6 |  | 0
63 | TRUE | TRUE | RfG_MaxRoCoF2 | 1.0651 | 0.7 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 10 | Frequency | 0 | 50 | -4 | Frequency | 0.08 |  | 0 | Frequency | 0.1 |  | 4 | Frequency | 0.2 |  | 0 | Frequency | 0.22 |  | 4 | Frequency | 0.3 |  | 0 | Frequency | 0.32 |  | -4 | Frequency | 0.42 |  | 0 | Frequency | 1 |  | -20 | Frequency | 1.02 |  | 0 | Frequency | 1.04 |  | 20 | Frequency | 1.06 |  | 0
64 | TRUE | TRUE | RfG_MaxRoCoF_CurveOF | 1.0651 | 0.7 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 20 | Frequency | 0 |  | 4 | Frequency | 0.05 |  | 2 | Frequency | 0.15 |  | 1 | Frequency | 0.9 |  | 0.35 | Frequency | 1.9 |  | 0 | Frequency | 3.9 |  | -1 | Frequency | 4.9 |  | 0
65 | TRUE | TRUE | RfG_MaxRoCoF_CurveUF | 1.0651 | 0.7 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 20 | Frequency | 0 |  | -4 | Frequency | 0.05 |  | -2 | Frequency | 0.15 |  | -1 | Frequency | 0.9 |  | -0.35 | Frequency | 1.9 |  | 0 | Frequency | 3.9 |  | 1 | Frequency | 4.9 |  | 0
66 | TRUE | TRUE | RfG_LVFRT_profile | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | -1 | 0 | Default | 20 | Voltage | 0 | 0 | 0 | Voltage | 0.1498 | 0 | 0 | Voltage | 0.1499 | 0 | 0 | Voltage | 0.15 | 0 | 0.62963 | Voltage | 1.5 | 0.85 | 0 | Voltage | 10 | 0.86 | 0
67 | TRUE | TRUE | RfG_LVFRT_profile_Pref_05 | 1.0651 | 0.5 | Default | LFSM | Default | 0 | Default | -1 | 0 | Default | 20 | Voltage | 0 | 0 | 0 | Voltage | 0.1498 | 0 | 0 | Voltage | 0.1499 | 0 | 0 | Voltage | 0.15 | 0 | 0.62963 | Voltage | 1.5 | 0.85 | 0 | Voltage | 10 | 0.86 | 0
68 | TRUE | TRUE | RfG_LVFRT_profil_Pref_05_Pavail | 1.0651 | 0.5 | 0.5 | LFSM | Default | 0 | Default | -1 | 0 | Default | 20 | Voltage | 0 | 0 | 0 | Voltage | 0.1498 | 0 | 0 | Voltage | 0.1499 | 0 | 0 | Voltage | 0.15 | 0 | 0.62963 | Voltage | 1.5 | 0.85 | 0 | Voltage | 10 | 0.86 | 0
69 | TRUE | TRUE | RfG_OVRT_profile | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | -1 | 0 | Default | 40 | Voltage | 0 | 1.3 |  | Voltage | 0.1 | 1.2 |  | Voltage | 20 | 1.15
70 | TRUE | TRUE | RfG_Fault_3_0 | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 3p fault | 0 | 0% | 0.15
71 | TRUE | TRUE | RfG_Fault_3_20 | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 3p fault | 0 | 20% | 0.45
72 | TRUE | TRUE | RfG_Fault_3_40 | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 3p fault | 0 | 40% | 0.75
73 | TRUE | TRUE | RfG_Fault_3_60 | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 3p fault | 0 | 60% | 1.05
74 | TRUE | TRUE | RfG_Fault_3_80 | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 3p fault | 0 | 80% | 1.35
75 | TRUE | TRUE | RfG_Fault_3_thres | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 3p fault | 0 | 85% | 1.35
76 | TRUE | TRUE | RfG_Fault_2_0 | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 2p-g fault | 0 | 0% | 0.15
77 | TRUE | TRUE | RfG_Fault_2_20 | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 2p-g fault | 0 | 20% | 0.45
78 | TRUE | TRUE | RfG_Fault_2_40 | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 2p-g fault | 0 | 40% | 0.75
79 | TRUE | TRUE | RfG_Fault_2_60 | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 2p-g fault | 0 | 60% | 1.05
80 | TRUE | TRUE | RfG_Fault_2_80 | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 2p-g fault | 0 | 80% | 1.35
81 | TRUE | TRUE | RfG_Fault_2_thres | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 2p-g fault | 0 | 85% | 1.35
82 | TRUE | TRUE | RfG_Fault_1_0 | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 1p fault | 0 | 0% | 0.15
83 | TRUE | TRUE | RfG_Fault_1_20 | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 1p fault | 0 | 20% | 0.45
84 | TRUE | TRUE | RfG_Fault_1_40 | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 1p fault | 0 | 40% | 0.75
85 | TRUE | TRUE | RfG_Fault_1_60 | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 1p fault | 0 | 60% | 1.05
86 | TRUE | TRUE | RfG_Fault_1_80 | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 1p fault | 0 | 80% | 1.35
87 | TRUE | TRUE | RfG_Fault_1_thres | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 1p fault | 0 | 85% | 1.35
88 | TRUE | TRUE | RfG_Voltage-support | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | -1 | 0 | Default | 5 | Voltage | 0 | 0.7 |  | Voltage | 0.2 | 0.5 |  | Voltage | 0.4 | 0.3 |  | Voltage | 0.6 | 1
89 | TRUE | TRUE | RfG_Fault_1_restrike | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 15 | 1p fault | 0 | 5% | 0.15 | 1p fault | 1.35 | 5% | 0.15 | 1p fault | 3 | 20% | 0.15 | 1p fault | 3.45 | 20% | 0.15
90 | TRUE | TRUE | RfG_Fault_3_double | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 15 | 3p fault | 0 | 10% | 0.15 | 3p fault | 1.65 | 20% | 0.15
91 | TRUE | TRUE | RfG_Fault_2_double | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 15 | 2p fault | 0 | 10% | 0.15 | 2p-g fault | 1.65 | 20% | 0.15
92 | TRUE | TRUE | RfG_Fault_3_SCR | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 20 | 15 | Default | 15 | 3p fault | 0 | 5% | 0.15 | SCR | 0.149 | 10 | 10
93 | TRUE | TRUE | RfG_Fault_2_SCR | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 20 | 15 | Default | 15 | 2p fault | 0 | 10% | 0.15 | SCR | 0.149 | 10 | 10
94 | TRUE | TRUE | RfG_LFSM-OU_step2 | 1.0651 | 0.5 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 160 | Frequency | 0 | 50.825 |  | Frequency | 20 | 50 |  | Frequency | 40 | 49.175 |  | Frequency | 60 | 50 |  | Frequency | 80 | 51.45 |  | Frequency | 100 | 50 |  | Frequency | 120 | 48.55 |  | Frequency | 140 | 50
95 | TRUE | TRUE | RfG_LFSM-OU_step1+FSM | 1.0651 | 0.7 | Default | LFSM+FSM | Default | 0 | Default | 10 | 10 | Default | 80 | Frequency | 0 | 51.5 |  | Frequency | 20 | 50 |  | Frequency | 40 | 48.5 |  | Frequency | 60 | 50
96 | TRUE | TRUE | RfG_FSM_rec_pstep | 1.0651 | 0.7 | Default | LFSM+FSM | Default | 0 | Default | 10 | 10 | Default |  | Frequency recording |  | recordings/DK1_frekvens.meas | 1 | Pref | 1 | 0 | 0
97 | TRUE | TRUE | RfG_LFSMO_ramp+pstep | 1.0651 | 0.5 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 40 | Frequency | 0 |  | 0.075 | Frequency | 15 |  | 0 | Pref | 0.1 | 1 |  | Frequency | 20 |  | -0.125 | Frequency | 29 | 50 | 0
98 | TRUE | TRUE | RfG_LFSM-O_Q_control | 1.0651 | 0.7 | Default | LFSM | Q | 0.1 | Default | 10 | 10 | Default | 40 | Qref | 0 | 0.25 |  | Frequency | 1 | 51 |  | Frequency | 25 | 50 |  | Qref | 27 | 0.1
99 | TRUE | TRUE | RfG_Ucontrol_LFSM-O | 1.0651 | 0.7 | Default | LFSM | Q(U) | 1.0651 | Default | 10 | 10 | Default | 15 | dVoltage | 0 | -0.1 |  | Frequency | 0.5 |  | 1 | Frequency | 1.5 | 51 | 0 | Frequency | 3.5 |  | -0.5 | Frequency | 5.5 | 50 | 0 | dVoltage | 5 | 0
100 | TRUE | TRUE | RfG_Ucontrol_Phasejump | 1.0651 | 0.7 | Default | LFSM | Q(U) | 1.0651 | Default | 10 | 10 | Default | 25 | Phase | 0 | 20 |  | dVoltage | 0.02 | -0.075 |  | dVoltage | 15 | 0
101 | TRUE | TRUE | RfG_Ucontrol_SCR | 1.0651 | 0.7 | Default | LFSM | Q(U) | 1.0651 | Default | 20 | 15 | Default | 25 | SCR | 0 | 10 | 10 | dVoltage | 0.1 | -0.075 |  | dVoltage | 15 | 0
102 | TRUE | TRUE | RfG_Ucontrol_Fault | 1.0651 | 0.7 | Default | LFSM | Q(U) | 1.0651 | Default | 10 | 10 | Default | 25 | 3p fault | 0 | 20% | 0.45 | dVoltage | 0.451 | -0.075 |  | dVoltage | 15 | 0
103 | TRUE | TRUE | RfG_Ucontrol_Fault_FRTlimit | 1.0651 | 0.7 | Default | LFSM | Q(U) | 1.0651 | Default | -1 | 0 | Default | 25 | Voltage | 0 | 0.2 |  | Voltage | 0.2 | 0.86 |  | Voltage | 15 | 1.0651
104 | TRUE | TRUE | RfG_Ucontrol_Scmin_Droop_2 | 1.0651 | 1 | Default | LFSM | Q(U) | 1.0651 | 2.0 | 10 | 10 | Default | 85 | dVoltage | 0 | 0.021303 |  | dVoltage | 7 | 0 |  | dVoltage | 14 | -0.021303 |  | dVoltage | 21 | 0 |  | dVoltage | 28 | 0.042605 |  | dVoltage | 35 | 0 |  | dVoltage | 42 | -0.042605 |  | dVoltage | 49 | 0 |  | dVoltage | 56 | 0.052868 |  | dVoltage | 63 | 0 |  | dVoltage | 70 | -0.097132 |  | dVoltage | 77 | 0
105 | TRUE | TRUE | RfG_Ucontrol_Scmin_Droop_4 | 1.0651 | 1 | Default | LFSM | Q(U) | 1.0651 | 4.0 | 10 | 10 | Default | 85 | dVoltage | 0 | 0.021303 |  | dVoltage | 7 | 0 |  | dVoltage | 14 | -0.021303 |  | dVoltage | 21 | 0 |  | dVoltage | 28 | 0.042605 |  | dVoltage | 35 | 0 |  | dVoltage | 42 | -0.042605 |  | dVoltage | 49 | 0 |  | dVoltage | 56 | 0.052868 |  | dVoltage | 63 | 0 |  | dVoltage | 70 | -0.097132 |  | dVoltage | 77 | 0
106 | TRUE | TRUE | RfG_Ucontrol_Scmin_Droop_7 | 1.0651 | 1 | Default | LFSM | Q(U) | 1.0651 | 7.0 | 10 | 10 | Default | 85 | dVoltage | 0 | 0.021303 |  | dVoltage | 7 | 0 |  | dVoltage | 14 | -0.021303 |  | dVoltage | 21 | 0 |  | dVoltage | 28 | 0.042605 |  | dVoltage | 35 | 0 |  | dVoltage | 42 | -0.042605 |  | dVoltage | 49 | 0 |  | dVoltage | 56 | 0.052868 |  | dVoltage | 63 | 0 |  | dVoltage | 70 | -0.097132 |  | dVoltage | 77 | 0
107 | TRUE | TRUE | RfG_Ucontrol_rec | 1.0651 | 1 | Default | LFSM | Q(U) | 1.0651 | Default | -1 | 0 | Default |  | Voltage recording |  | recordings/DK1_Voltage.csv | 1.0651
108 | TRUE | TRUE | RfG_Pavail_variation | 1.0651 | 1 | 1 | LFSM | Default | 0 | Default | 10 | 10 | Default | 20 | Pavail | 1 | 0.75 |  | Pavail | 5 | 0.25 |  | Pavail | 10 | 1
109 | TRUE | TRUE | RfG_Pavail_step_P_step_up_05_10 | 1.0651 | 0.5 | 0.5 | LFSM | Default | 0 | Default | 10 | 10 | Default | 175 | Pref | 0 | 1 | 0 | Pavail | 40 | 1 | 0
110 | TRUE | TRUE | RfG_MaxPhaseJump_Extreme | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 20 | Phase | 0 | 30 |  | Phase | 2.5 | 0 |  | Phase | 5 | -40 |  | Phase | 7.5 | 0
111 | TRUE | TRUE | RfG_RoCoF_ACER-CurveOF | 1.0651 | 0.7 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | Frequency | 0 |  | 4 | Frequency | 0.25 |  | 1.3333 | Frequency | 1 |  | 0.33333 | Frequency | 2.5 |  | 0 | Frequency | 4.5 |  | -1 | Frequency | 5.5 |  | 0
112 | TRUE | TRUE | RfG_RoCoF_ACER-CurveUF | 1.0651 | 0.7 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | Frequency | 0 |  | -4 | Frequency | 0.25 |  | -1.33 | Frequency | 1 |  | -0.333 | Frequency | 2.5 |  | 0 | Frequency | 4.5 |  | 1 | Frequency | 6 |  | 0
113 | TRUE | TRUE | RfG_RoCoF+PhaseJump1 | 1.0651 | 0.7 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | Frequency | 0 | 50 | -1 | Frequency | 0.02 |  | 0 | Phase | 0.021 | -20 |  | Frequency | 0.04 |  | -1 | Frequency | 0.06 |  | 1 | Frequency | 0.08 |  | -1 | Frequency | 0.1 |  | 1 | Frequency | 0.14 |  | 0 | Phase | 0.141 | 0 |  | Frequency | 0.16 |  | -1 | Frequency | 0.18 |  | 0
114 | TRUE | TRUE | RfG_RoCoF+PhaseJump2 | 1.0651 | 0.7 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | Frequency | 0 | 50 | -1 | Frequency | 0.02 |  | 0 | Phase | 0.021 | 20 |  | Frequency | 0.04 |  | -1 | Frequency | 0.06 |  | 1 | Frequency | 0.08 |  | -1 | Frequency | 0.1 |  | 1 | Frequency | 0.14 |  | 0 | Phase | 0.141 | 0 |  | Frequency | 0.16 |  | -1 | Frequency | 0.18 |  | 0
115 | TRUE | TRUE | RfG_Fault_3_0_NotDef | 1.0651 | 1 | Default | LFSM | Q(U) | 1.0651 | Default | 10 | 10 | Default | 12 | 3p fault | 0 | 0% | 0.15
116 | TRUE | TRUE | RfG_Fault_3_20_NotDef | 1.0651 | 1 | Default | LFSM | Q(U) | 1.0651 | Default | 10 | 10 | Default | 12 | 3p fault | 0 | 20% | 0.45
117 | TRUE | TRUE | RfG_Fault_3_40_NotDef | 1.0651 | 1 | Default | LFSM | Q(U) | 1.0651 | Default | 10 | 10 | Default | 12 | 3p fault | 0 | 40% | 0.75
118 | TRUE | TRUE | RfG_Fault_3_60_NotDef | 1.0651 | 1 | Default | LFSM | Q(U) | 1.0651 | Default | 10 | 10 | Default | 12 | 3p fault | 0 | 60% | 1.05
119 | TRUE | TRUE | RfG_Fault_3_80_NotDef | 1.0651 | 1 | Default | LFSM | Q(U) | 1.0651 | Default | 10 | 10 | Default | 12 | 3p fault | 0 | 80% | 1.35
120 | TRUE | TRUE | RfG_Fault_3_thres_NotDef | 1.0651 | 1 | Default | LFSM | Q(U) | 1.0651 | Default | 10 | 10 | Default | 12 | 3p fault | 0 | 85% | 1.35
121 | TRUE | TRUE | RfG_Fault_2_20_NotDef | 1.0651 | 1 | Default | LFSM | Q(U) | 1.0651 | Default | 10 | 10 | Default | 12 | 2p-g fault | 0 | 20% | 0.45
122 | TRUE | TRUE | RfG_Fault_2_40_NotDef | 1.0651 | 1 | Default | LFSM | Q(U) | 1.0651 | Default | 10 | 10 | Default | 12 | 2p-g fault | 0 | 40% | 0.75
123 | TRUE | TRUE | RfG_Fault_2_60_NotDef | 1.0651 | 1 | Default | LFSM | Q(U) | 1.0651 | Default | 10 | 10 | Default | 12 | 2p-g fault | 0 | 60% | 1.05
124 | TRUE | TRUE | RfG_Fault_2_80_NotDef | 1.0651 | 1 | Default | LFSM | Q(U) | 1.0651 | Default | 10 | 10 | Default | 12 | 2p-g fault | 0 | 80% | 1.35
125 | TRUE | TRUE | RfG_Fault_1_20_NotDef | 1.0651 | 1 | Default | LFSM | Q(U) | 1.0651 | Default | 10 | 10 | Default | 12 | 1p fault | 0 | 20% | 0.45
126 | TRUE | TRUE | RfG_Fault_1_40_NotDef | 1.0651 | 1 | Default | LFSM | Q(U) | 1.0651 | Default | 10 | 10 | Default | 12 | 1p fault | 0 | 40% | 0.75
127 | TRUE | TRUE | RfG_Fault_1_60_NotDef | 1.0651 | 1 | Default | LFSM | Q(U) | 1.0651 | Default | 10 | 10 | Default | 12 | 1p fault | 0 | 60% | 1.05
128 | TRUE | TRUE | RfG_Fault_1_80_NotDef | 1.0651 | 1 | Default | LFSM | Q(U) | 1.0651 | Default | 10 | 10 | Default | 12 | 1p fault | 0 | 80% | 1.35
129 | TRUE | TRUE | RfG_Fault_3_SCR_NotDef | 1.0651 | 1 | Default | LFSM | Q(U) | 1.0651 | Default | 20 | 15 | Default | 15 | 3p fault | 0 | 5% | 0.15 | SCR | 0.149 | 10 | 10
130 | TRUE | TRUE | RfG_Fault_2_SCR_NotDef | 1.0651 | 1 | Default | LFSM | Q(U) | 1.0651 | Default | 20 | 15 | Default | 15 | 2p fault | 0 | 10% | 0.15 | SCR | 0.149 | 10 | 10
131 | TRUE | TRUE | RfG_Fault_3_UnderThres_NotDef | 1.0651 | 1 | Default | LFSM | Q(U) | 1.0651 | Default | 10 | 10 | Default | 12 | 3p fault | 0 | 83% | 1.35
132 | TRUE | TRUE | RfG_Fault_3_UnderThres | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 3p fault | 0 | 83% | 1.35
133 | TRUE | TRUE | RfG_Fault_1_UnderThres | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 1p fault | 0 | 83% | 1.35
134 | TRUE | TRUE | RfG_Fault_2_double_NotDef | 1.0651 | 1 | Default | LFSM | Q(U) | 1.0651 | Default | 10 | 10 | Default | 15 | 2p fault | 0 | 10% | 0.15 | 2p-g fault | 1.65 | 20% | 0.15
135 | TRUE | TRUE | RfG_Fault_double-mix_SCR | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 20 | 15 | Default | 15 | 2p fault | 0 | 30% | 0.15 | 3p fault | 1.65 | 30% | 0.15 | SCR | 1.799 | 10 | 10
136 | TRUE | TRUE | RfG_Fault_3_20_WG | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 2 | 3 | Default | 20 | 3p fault | 0 | 20% | 0.2
137 | TRUE | TRUE | RfG_Fault_2_20_WG | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 2 | 3 | Default | 20 | 2p-g fault | 0 | 20% | 0.2
138 | TRUE | TRUE | RfG_Fault_3_RoCoF_curveOF | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 15 | 3p fault | 0 | 40% | 0.2 | Frequency | 1.21 |  | 4 | Frequency | 1.26 |  | 2 | Frequency | 1.36 |  | 1 | Frequency | 2.11 |  | 0.35 | Frequency | 3.11 |  | 0 | Frequency | 5.11 |  | -1 | Frequency | 6.11 |  | 0
139 | TRUE | TRUE | RfG_Fault_3_RoCoF_curveUF | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 15 | 3p fault | 0 | 40% | 0.2 | Frequency | 1.21 |  | -4 | Frequency | 1.26 |  | -2 | Frequency | 1.36 |  | -1 | Frequency | 2.11 |  | -0.35 | Frequency | 3.11 |  | 0 | Frequency | 5.11 |  | 1 | Frequency | 6.11 |  | 0
140 | TRUE | TRUE | RfG_Fault_3_SCR_freqStep1 | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 20 | 15 | Default | 20 | 3p fault | 0 | 40% | 0.2 | SCR | 0.199 | 10 | 10 | Frequency | 0.205 | 51 |  | Frequency | 6 | 50
141 | TRUE | TRUE | RfG_Fault_3_SCR_freqStep2 | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 20 | 15 | Default | 20 | 3p fault | 0 | 40% | 0.2 | SCR | 0.199 | 10 | 10 | Frequency | 0.205 | 51 |  | Frequency | 4 | 50
142 | TRUE | TRUE | RfG_SCR_step_Max-Min | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 30 | 20 | Default | 10 | SCR | 0 | 10 | 10 | SCR | 5 | 30 | 20
143 | TRUE | TRUE | RfG_SCR_step_Max-Min_NotDef | 1.0651 | 1 | Default | LFSM | Q(U) | 1.0651 | Default | 30 | 20 | Default | 10 | SCR | 0 | 10 | 10 | SCR | 5 | 30 | 20
144 | TRUE | TRUE | RfG_Fault_rec_1_Q | 1.0651 | 1 | Default | LFSM | Q | 0 | Default | -1 | 0 | Default |  | Voltage recording |  | recordings/DK1_fault1.csv | 1.0651
145 | TRUE | TRUE | RfG_Fault_rec_1_Q(U) | 1.0651 | 1 | Default | LFSM | Q(U) | 1.0651 | Default | -1 | 0 | Default |  | Voltage recording |  | recordings/DK1_fault1.csv | 1.0651
146 | TRUE | TRUE | RfG_Fault_rec_2_Q | 1.0651 | 1 | Default | LFSM | Q | 0 | Default | -1 | 0 | Default |  | Voltage recording |  | recordings/DK1_fault2.meas | 1.0651
147 | TRUE | TRUE | RfG_Fault_rec_2_Q(U) | 1.0651 | 1 | Default | LFSM | Q(U) | 1.0651 | Default | -1 | 0 | Default |  | Voltage recording |  | recordings/DK1_fault2.meas | 1.0651
148 | TRUE | TRUE | RfG_Fault_rec_3_Q | 1.0651 | 1 | Default | LFSM | Q | 0 | Default | -1 | 0 | Default |  | Voltage recording |  | recordings/slow_recovery.csv | 1.0651
149 | TRUE | TRUE | RfG_Fault_rec_3_Q(U) | 1.0651 | 1 | Default | LFSM | Q(U) | 1.0651 | Default | -1 | 0 | Default |  | Voltage recording |  | recordings/slow_recovery.csv | 1.0651
150 | TRUE | TRUE | RfG_TRF_GND_Fault_3_0.20pu_Scmin | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Grounded | 12 | 3p fault | 0 | 0.2 | 0.45
151 | TRUE | TRUE | RfG_TRF_GND_Fault_3_0.20pu_Scmax | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 30 | 20 | Grounded | 12 | 3p fault | 0 | 0.2 | 0.45
152 | TRUE | TRUE | RfG_TRF_GND_Fault_2_0.20pu_Scmin | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Grounded | 12 | 2p fault | 0 | 0.2 | 0.45
153 | TRUE | TRUE | RfG_TRF_GND_Fault_2_0.20pu_Scmax | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 30 | 20 | Grounded | 12 | 2p fault | 0 | 0.2 | 0.45
154 | TRUE | TRUE | RfG_TRF_GND_Fault_2g_0.20pu_Scmin | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Grounded | 12 | 2p-g fault | 0 | 0.2 | 0.45
155 | TRUE | TRUE | RfG_TRF_GND_Fault_2g_0.20pu_Scmax | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 30 | 20 | Grounded | 12 | 2p-g fault | 0 | 0.2 | 0.45
156 | TRUE | TRUE | RfG_TRF_GND_Fault_1_0.20pu_Scmin | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Grounded | 12 | 1p fault | 0 | 0.2 | 0.45
157 | TRUE | TRUE | RfG_TRF_GND_Fault_1_0.20pu_Scmax | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 30 | 20 | Grounded | 12 | 1p fault | 0 | 0.2 | 0.45
158 | TRUE | TRUE | RfG_Shift_05_Fault_3_0.20pu | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 3p fault | 0.005 | 20% | 0.06
159 | TRUE | TRUE | RfG_Shift_55_Fault_3_0.40pu | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 3p fault | 0.055 | 40% | 0.06
160 | TRUE | TRUE | RfG_Pavail_Fault_3_0.20pu | 1.0651 | 0.5 | 0.5 | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 3p fault | 0 | 0.2 | 0.45
161 | TRUE | TRUE | RfG_Pavail_Fault_2_0.20pu | 1.0651 | 0.5 | 0.5 | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 2p-g fault | 0 | 0.2 | 0.45
162 | TRUE | TRUE | RfG_proc_VoltageRise_1.2 | 1.0651 | 1 | Default | LFSM | Q | 0 | Default | 10 | 10 | Default | 60 | dVoltage | 0 | 0.2 | 0
163 | TRUE | TRUE | RfG_proc_VoltageRise_1.3 | 1.0651 | 1 | Default | LFSM | Q | 0 | Default | 10 | 10 | Default | 60 | dVoltage | 0 | 0.3 | 0
164 | TRUE | TRUE | RfG_proc_VoltageRise_1.4 | 1.0651 | 1 | Default | LFSM | Q | 0 | Default | 10 | 10 | Default | 60 | dVoltage | 0 | 0.4 | 0
165 | TRUE | TRUE | RfG_proc_VoltageRise_1.5 | 1.0651 | 1 | Default | LFSM | Q | 0 | Default | 10 | 10 | Default | 60 | dVoltage | 0 | 0.5 | 0
166 | TRUE | TRUE | RfG_proc_VoltageRise_insta_min | 1.0651 | 1 | Default | LFSM | Q | 0 | Default | 10 | 10 | Default | 18 | dVoltage | 0 | 0.3 | 0 | dVoltage | 0.1 | 0 |  | dVoltage | 3 | 0.5 |  | dVoltage | 3.1 | 0 |  | dVoltage | 6 | 0.7 |  | dVoltage | 6.1 | 0 |  | dVoltage | 9 | 0.9 |  | dVoltage | 9.1 | 0 |  | dVoltage | 12 | 1.1 |  | dVoltage | 12.1 | 0 |  | dVoltage | 15 | 1.3 |  | dVoltage | 15.1 | 0
167 | TRUE | TRUE | RfG_proc_VoltageRise_insta_max | 1.0651 | 1 | Default | LFSM | Q | 0 | Default | 30 | 20 | Default | 18 | dVoltage | 0 | 0.3 | 0 | dVoltage | 0.1 | 0 |  | dVoltage | 3 | 0.5 |  | dVoltage | 3.1 | 0 |  | dVoltage | 6 | 0.7 |  | dVoltage | 6.1 | 0 |  | dVoltage | 9 | 0.9 |  | dVoltage | 9.1 | 0 |  | dVoltage | 12 | 1.1 |  | dVoltage | 12.1 | 0 |  | dVoltage | 15 | 1.3 |  | dVoltage | 15.1 | 0
168 | TRUE | TRUE | RfG_proc_Fault_3_0.8pu | 1.0651 | 1 | Default | LFSM | Q | 0 | Default | 10 | 10 | Default | 60 | 3p fault | 0 | 80% | 60
169 | TRUE | TRUE | RfG_proc_Fault_3_0.6pu | 1.0651 | 1 | Default | LFSM | Q | 0 | Default | 10 | 10 | Default | 60 | 3p fault | 0 | 60% | 60
170 | TRUE | TRUE | RfG_proc_Fault_3_0.40pu | 1.0651 | 1 | Default | LFSM | Q | 0 | Default | 10 | 10 | Default | 60 | 3p fault | 0 | 40% | 60
171 | TRUE | TRUE | RfG_proc_Fault_3_0.20pu | 1.0651 | 1 | Default | LFSM | Q | 0 | Default | 10 | 10 | Default | 60 | 3p fault | 0 | 20% | 60
172 | TRUE | TRUE | RfG_proc_Freq_51.6Hz | 1.0651 | 0.7 | Default | LFSM | Q | 0 | Default | 10 | 10 | Default | 60 | Frequency | 0 | 51.6
173 | TRUE | TRUE | RfG_proc_Freq_47.4Hz | 1.0651 | 0.7 | Default | LFSM | Q | 0 | Default | 10 | 10 | Default | 60 | Frequency | 0 | 47.4
174 | TRUE | TRUE | RfG_proc_Freq_limit_up | 1.0651 | 0.7 | Default | LFSM | Q | 0 | Default | 10 | 10 | Default | 40 | Frequency | 0 | 52 |  | Frequency | 8 | 53 |  | Frequency | 16 | 54 |  | Frequency | 24 | 55 |  | Frequency | 32 | 56 |  | Frequency | 35 | 50
175 | TRUE | TRUE | RfG_proc_Freq_limit_down | 1.0651 | 0.7 | Default | LFSM | Q | 0 | Default | 10 | 10 | Default | 40 | Frequency | 0 | 47 |  | Frequency | 8 | 46 |  | Frequency | 16 | 45 |  | Frequency | 24 | 44 |  | Frequency | 32 | 43 |  | Frequency | 35 | 50
176 | TRUE | TRUE | RfG_proc_Fault_1_0.05pu | 1.0651 | 1 | Default | LFSM | Q | 0 | Default | 10 | 10 | Grounded | 60 | 1p fault | 0 | 0.05 | 60

## DCC cases
Case |  |  |  | Initial Settings | [9 empty] | Event 1 |  |  |  | Event 2 |  |  |  | Event 3 |  |  |  | Event 4 |  |  |  | Event 5 |  |  |  | Event 6 |  |  |  | Event 7 |  |  |  | Event 8 |  |  |  | Event 9 |  |  |  | Event 10 |  |  |  | Event 11 |  |  |  | Event 12
Rank | RMS | EMT | Name | U0 | P0 | Pmode | Qmode | Qref0 | QUdroop0 | SCR0 | XR0 | MtrfrGnd0 | Simulationtime | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2
1001 | TRUE | TRUE | DCC_SS_flatrun_Q1 | 1.0651 | 0 | No P(f) | Default | 0 | Default | 10 | 10 | Default | 60 | PF disconnect all ref.
1002 | TRUE | TRUE | DCC_SS_flatrun_Q2 | 1.0651 | 0.25 | No P(f) | Default | 0 | Default | 10 | 10 | Default | 60 | PF disconnect all ref.
1003 | TRUE | TRUE | DCC_SS_flatrun_Q3 | 1.0651 | 0.5 | No P(f) | Default | 0 | Default | 10 | 10 | Default | 60 | PF disconnect all ref.
1004 | TRUE | TRUE | DCC_SS_flatrun_Q4 | 1.0651 | 0.75 | No P(f) | Default | 0 | Default | 10 | 10 | Default | 60 | PF disconnect all ref.
1005 | TRUE | TRUE | DCC_SS_flatrun_Q5 | 1.0651 | 1 | No P(f) | Default | 0 | Default | 10 | 10 | Default | 60 | PF disconnect all ref.
1006 | TRUE | TRUE | DCC_Fault_3_0 | 1.0651 | 1 | No P(f) | Default | 0 | Default | 10 | 10 | Default | 12 | 3p fault | 0 | 0% | 0.15
1007 | TRUE | TRUE | DCC_Fault_3_20 | 1.0651 | 1 | No P(f) | Default | 0 | Default | 10 | 10 | Default | 12 | 3p fault | 0 | 20% | 0.45
1008 | TRUE | TRUE | DCC_Fault_3_40 | 1.0651 | 1 | No P(f) | Default | 0 | Default | 10 | 10 | Default | 12 | 3p fault | 0 | 40% | 0.75
1009 | TRUE | TRUE | DCC_Fault_3_80 | 1.0651 | 1 | No P(f) | Default | 0 | Default | 10 | 10 | Default | 12 | 3p fault | 0 | 80% | 1.35
1010 | TRUE | TRUE | DCC_Fault_2_0 | 1.0651 | 1 | No P(f) | Default | 0 | Default | 10 | 10 | Default | 12 | 2p-g fault | 0 | 0% | 0.15
1011 | TRUE | TRUE | DCC_Fault_2_20 | 1.0651 | 1 | No P(f) | Default | 0 | Default | 10 | 10 | Default | 12 | 2p-g fault | 0 | 20% | 0.45
1012 | TRUE | TRUE | DCC_Fault_2_40 | 1.0651 | 1 | No P(f) | Default | 0 | Default | 10 | 10 | Default | 12 | 2p-g fault | 0 | 40% | 0.75
1013 | TRUE | TRUE | DCC_Fault_2_80 | 1.0651 | 1 | No P(f) | Default | 0 | Default | 10 | 10 | Default | 12 | 2p-g fault | 0 | 80% | 1.35
1014 | TRUE | TRUE | DCC_Fault_1_0 | 1.0651 | 1 | No P(f) | Default | 0 | Default | 10 | 10 | Default | 12 | 1p fault | 0 | 0% | 0.15
1015 | TRUE | TRUE | DCC_Fault_1_20 | 1.0651 | 1 | No P(f) | Default | 0 | Default | 10 | 10 | Default | 12 | 1p fault | 0 | 20% | 0.45
1016 | TRUE | TRUE | DCC_Fault_1_40 | 1.0651 | 1 | No P(f) | Default | 0 | Default | 10 | 10 | Default | 12 | 1p fault | 0 | 40% | 0.75
1017 | TRUE | TRUE | DCC_Fault_1_80 | 1.0651 | 1 | No P(f) | Default | 0 | Default | 10 | 10 | Default | 12 | 1p fault | 0 | 80% | 1.35
1018 | TRUE | TRUE | DCC_Fault_1_restrike | 1.0651 | 1 | No P(f) | Default | 0 | Default | 10 | 10 | Default | 15 | 1p fault | 0 | 5% | 0.15 | 1p fault | 1.35 | 5% | 0.15 | 1p fault | 3 | 20% | 0.15 | 1p fault | 3.45 | 20% | 0.15
1019 | TRUE | TRUE | DCC_Fault_3_double | 1.0651 | 1 | No P(f) | Default | 0 | Default | 10 | 10 | Default | 15 | 3p fault | 0 | 10% | 0.15 | 3p fault | 1.65 | 20% | 0.15
1020 | TRUE | TRUE | DCC_Fault_2_double | 1.0651 | 1 | No P(f) | Default | 0 | Default | 10 | 10 | Default | 15 | 2p fault | 0 | 10% | 0.15 | 2p-g fault | 1.65 | 20% | 0.15
1021 | TRUE | TRUE | DCC_Fault_3_20_short | 1.0651 | 1 | No P(f) | Default | 0 | Default | 10 | 10 | Default | 2 | 3p fault | 0 | 20% | 0.25 | SCR | 0.249 | 10 | 10
1022 | TRUE | TRUE | DCC_Fault_2_20_short | 1.0651 | 1 | No P(f) | Default | 0 | Default | 10 | 10 | Default | 2 | 2p-g fault | 0 | 20% | 0.25
1023 | TRUE | TRUE | DCC_Fault_3_20_WG | 1.0651 | 1 | No P(f) | Default | 0 | Default | 2 | 3 | Default | 12 | 3p fault | 0 | 20% | 0.2
1024 | TRUE | TRUE | DCC_Fault_2_20_WG | 1.0651 | 1 | No P(f) | Default | 0 | Default | 2 | 3 | Default | 12 | 2p-g fault | 0 | 20% | 0.2
1025 | TRUE | TRUE | DCC_Fault_3_SCR | 1.0651 | 1 | No P(f) | Default | 0 | Default | 20 | 15 | Default | 12 | 3p fault | 0 | 5% | 0.15 | SCR | 0.149 | 10 | 10
1026 | TRUE | TRUE | DCC_Fault_2_SCR | 1.0651 | 1 | No P(f) | Default | 0 | Default | 20 | 15 | Default | 12 | 2p fault | 0 | 10% | 0.15 | SCR | 0.149 | 10 | 10
1027 | TRUE | TRUE | DCC_Fault_3_SCR_freqStep | 1.0651 | 1 | No P(f) | Default | 0 | Default | 20 | 15 | Default | 12 | 3p fault | 0 | 40% | 0.2 | SCR | 0.199 | 10 | 10 | Frequency | 0.205 | 51 |  | Frequency | 5.5 | 50
1028 | TRUE | TRUE | DCC_FRTsensitivity | 1 | 1 | No P(f) | Default | 0 | Default | -1 | 0 | Default | 85 | Voltage | 2 | 0.85 |  | Voltage | 8 | 1 |  | Voltage | 20 | 0.84 |  | Voltage | 26 | 1 |  | Voltage | 40 | 0.86 |  | Voltage | 46 | 0.8 |  | Voltage | 51 | 1 |  | Voltage | 65 | 0.86 |  | Voltage | 71 | 0.75 |  | Voltage | 73 | 1
1029 | TRUE | TRUE | DCC_FRTsensitivity-ramp | 1 | 1 | No P(f) | Default | 0 | Default | -1 | 0 | Default | 20 | dVoltage | 2 |  | -0.05 | dVoltage | 6 | -0.2 | 0 | dVoltage | 11 |  | 0.1 | dVoltage | 13 | 0 | 0
1030 | TRUE | TRUE | DCC_SCR_step_Max-Min | 1.0651 | 1 | No P(f) | Default | 0 | Default | 30 | 20 | Default | 10 | SCR | 0 | 10 | 10 | SCR | 5 | 30 | 20
1031 | TRUE | TRUE | DCC_LVFRT(kat7)_Profile | 1.0651 | 1 | No P(f) | Default | 0 | Default | -1 | 0 | Default | 20 | Voltage | 0 | 0 | 0 | Voltage | 0.15 | 0.35 | 0 | Voltage | 0.55 | 0.35 | 0.57895 | Voltage | 1.5 | 0.9 | 0
1032 | TRUE | TRUE | DCC_OVFRT(SP)_Profile | 1.0651 | 1 | No P(f) | Default | 0 | Default | -1 | 0 | Default | 50 | Voltage | 0 | 1.3 |  | Voltage | 0.1 | 1.2 |  | Voltage | 20 | 1.15
1033 | TRUE | TRUE | DCC_Fault_rec_1_Q | 1.0651 | 1 | No P(f) | Default | 0 | Default | -1 | 0 | Default |  | Voltage recording |  | recordings/DK1_fault1.csv | 1.0651
1034 | TRUE | TRUE | DCC_Fault_rec_3_Q | 1.0651 | 1 | No P(f) | Default | 0 | Default | -1 | 0 | Default |  | Voltage recording |  | recordings/slow_recovery.csv | 1.0651
1035 | TRUE | TRUE | DCC_TRF_GND_Fault_3_0.20pu_Scmin | 1.0651 | 1 | No P(f) | Default | 0 | Default | 10 | 10 | Grounded | 12 | 3p fault | 0 | 0.2 | 0.45
1036 | TRUE | TRUE | DCC_TRF_GND_Fault_3_0.20pu_Scmax | 1.0651 | 1 | No P(f) | Default | 0 | Default | 30 | 20 | Grounded | 12 | 3p fault | 0 | 0.2 | 0.45
1037 | TRUE | TRUE | DCC_TRF_GND_Fault_2_0.20pu_Scmin | 1.0651 | 1 | No P(f) | Default | 0 | Default | 10 | 10 | Grounded | 12 | 2p fault | 0 | 0.2 | 0.45
1038 | TRUE | TRUE | DCC_TRF_GND_Fault_2_0.20pu_Scmax | 1.0651 | 1 | No P(f) | Default | 0 | Default | 30 | 20 | Grounded | 12 | 2p fault | 0 | 0.2 | 0.45
1039 | TRUE | TRUE | DCC_TRF_GND_Fault_2g_0.20pu_Scmin | 1.0651 | 1 | No P(f) | Default | 0 | Default | 10 | 10 | Grounded | 12 | 2p-g fault | 0 | 0.2 | 0.45
1040 | TRUE | TRUE | DCC_TRF_GND_Fault_2g_0.20pu_Scmax | 1.0651 | 1 | No P(f) | Default | 0 | Default | 30 | 20 | Grounded | 12 | 2p-g fault | 0 | 0.2 | 0.45
1041 | TRUE | TRUE | DCC_TRF_GND_Fault_1_0.20pu_Scmin | 1.0651 | 1 | No P(f) | Default | 0 | Default | 10 | 10 | Grounded | 12 | 1p fault | 0 | 0.2 | 0.45
1042 | TRUE | TRUE | DCC_TRF_GND_Fault_1_0.20pu_Scmax | 1.0651 | 1 | No P(f) | Default | 0 | Default | 30 | 20 | Grounded | 12 | 1p fault | 0 | 0.2 | 0.45
1043 | TRUE | TRUE | DCC_SystemGuard | 1.0651 | 1 | No P(f) | Default | 0 | Default | 10 | 10 | Default | 45 | Signal 1 | -1 | 0 |  | Signal 3 | 0 | 1 |  | Signal 1 | 1 | 2 |  | Signal 1 | 15 | 4 |  | Signal 1 | 30 | 0
1044 | TRUE | TRUE | DCC_SystemGuard+fault | 1.0651 | 1 | No P(f) | Default | 0 | Default | 10 | 10 | Default | 45 | Signal 1 | -1 | 0 |  | Signal 3 | 0 | 1 |  | 3p fault | 1 | 0.2 | 0.45 | Signal 1 | 1.65 | 4 |  | Signal 1 | 30 | 0
1045 | TRUE | TRUE | DCC_MaxPhaseJump | 1.0651 | 1 | No P(f) | Default | 0 | Default | 10 | 10 | Default | 10 | Phase | 0 | 20 |  | Phase | 2.5 | 0 |  | Phase | 5 | -20 |  | Phase | 7.5 | 0
1046 | TRUE | TRUE | DCC_MaxPhaseJump2 | 1.0651 | 1 | No P(f) | Default | 0 | Default | 10 | 10 | Default | 5 | Phase | 0 | 6.5 |  | Phase | 0.02 | 13.25 |  | Phase | 0.04 | 20 |  | Phase | 2.5 | 13.5 |  | Phase | 2.52 | 6.75 |  | Phase | 2.54 | 0
1047 | TRUE | TRUE | DCC_MaxRoCoF1 | 1.0651 | 1 | No P(f) | Default | 0 | Default | 10 | 10 | Default | 10 | Frequency | 0 | 50 | 2 | Frequency | 0.5 |  | -2 | Frequency | 1 |  | 0 | Frequency | 2 | 50 | -0.5 | Frequency | 4 |  | 0.5 | Frequency | 6 |  | 0
1048 | TRUE | TRUE | DCC_MaxRoCoF2 | 1.0651 | 1 | No P(f) | Default | 0 | Default | 10 | 10 | Default | 5 | Frequency | 0 | 50 | -4 | Frequency | 0.08 |  | 0 | Frequency | 0.1 |  | 4 | Frequency | 0.2 | 50 | 0 | Frequency | 0.22 |  | 4 | Frequency | 0.3 |  | 0 | Frequency | 0.32 |  | -4 | Frequency | 0.42 |  | 0 | Frequency | 1 |  | -20 | Frequency | 1.02 |  | 0 | Frequency | 1.04 |  | 20 | Frequency | 1.06 |  | 0
1049 | TRUE | TRUE | DCC_MaxRoCoF_CurveOF | 1.0651 | 1 | No P(f) | Default | 0 | Default | 10 | 10 | Default | 10 | Frequency | 0 |  | 4 | Frequency | 0.05 |  | 2 | Frequency | 0.15 |  | 1 | Frequency | 0.9 |  | 0.35 | Frequency | 1.9 |  | 0 | Frequency | 3.9 |  | -1 | Frequency | 4.9 |  | 0
1050 | TRUE | TRUE | DCC_MaxRoCoF_CurveUF | 1.0651 | 1 | No P(f) | Default | 0 | Default | 10 | 10 | Default | 10 | Frequency | 0 |  | -4 | Frequency | 0.05 |  | -2 | Frequency | 0.15 |  | -1 | Frequency | 0.9 |  | -0.35 | Frequency | 1.9 |  | 0 | Frequency | 3.9 |  | 1 | Frequency | 4.9 |  | 0
1051 | TRUE | TRUE | DCC_MaxPhaseJump_Extreme_min | 1.0651 | 1 | No P(f) | Default | 0 | Default | 10 | 10 | Default | 30 | Phase | 0 | 30 |  | Phase | 2.5 | 0 |  | Phase | 5 | 40 |  | Phase | 7.5 | 0 |  | Phase | 10 | 50 |  | Phase | 12.5 | 0 |  | Phase | 15 | 60 |  | Phase | 17.5 | 0 |  | Phase | 20 | 70 |  | Phase | 22.5 | 0
1052 | TRUE | TRUE | DCC_MaxPhaseJump_Extreme_max | 1.0651 | 1 | No P(f) | Default | 0 | Default | 30 | 20 | Default | 30 | Phase | 0 | 30 |  | Phase | 2.5 | 0 |  | Phase | 5 | 40 |  | Phase | 7.5 | 0 |  | Phase | 10 | 50 |  | Phase | 12.5 | 0 |  | Phase | 15 | 60 |  | Phase | 17.5 | 0 |  | Phase | 20 | 70 |  | Phase | 22.5 | 0
1053 | TRUE | TRUE | DCC_RoCoF+PhaseJump1 | 1.0651 | 0.7 | No P(f) | Default | 0 | Default | 10 | 10 | Default | 12 | Frequency | 0 | 50 | -1 | Frequency | 0.02 |  | 0 | Phase | 0.021 | -20 |  | Frequency | 0.04 |  | -1 | Frequency | 0.06 |  | 1 | Frequency | 0.08 |  | -1 | Frequency | 0.1 |  | 1 | Frequency | 0.14 |  | 0 | Phase | 0.141 | 0 |  | Frequency | 0.16 |  | -1 | Frequency | 0.18 |  | 0
1054 | TRUE | TRUE | DCC_RoCoF+PhaseJump2 | 1.0651 | 0.7 | No P(f) | Default | 0 | Default | 10 | 10 | Default | 12 | Frequency | 0 | 50 | -1 | Frequency | 0.02 |  | 0 | Phase | 0.021 | 20 |  | Frequency | 0.04 |  | -1 | Frequency | 0.06 |  | 1 | Frequency | 0.08 |  | -1 | Frequency | 0.1 |  | 1 | Frequency | 0.14 |  | 0 | Phase | 0.141 | 0 |  | Frequency | 0.16 |  | -1 | Frequency | 0.18 |  | 0
1055 | TRUE | TRUE | DCC_LFSM-OU_step1 | 1.0651 | 0.7 | No P(f) | Default | 0 | Default | 10 | 10 | Default | 100 | Frequency | 0 | 51.5 |  | Frequency | 20 | 50 |  | Frequency | 40 | 48.5 |  | Frequency | 60 | 47.5 |  | Frequency | 80 | 50
1056 | TRUE | TRUE | DCC_LFSM-O_ramp | 1.0651 | 1 | No P(f) | Default | 0 | Default | 10 | 10 | Default | 21.5 | Frequency | 0 |  | 0.5 | Frequency | 3 | 51.5 | 0 | Frequency | 5 |  | -0.2 | Frequency | 11.5 | 50.2 | 0
1057 | TRUE | TRUE | DCC_LFSM-U_ramp | 1.0651 | 1 | No P(f) | Default | 0 | Default | 10 | 10 | Default | 21.5 | Frequency | 0 |  | -0.5 | Frequency | 3 | 48.5 | 0 | Frequency | 5 |  | 0.2 | Frequency | 11.5 | 49.8 | 0
1058 | TRUE | TRUE | DCC_LFDD | 1.0651 | 1 | No P(f) | Default | 0 | Default | 10 | 10 | Default | 60 | Frequency | 0 | 48.9 |  | Frequency | 10 | 48.8 |  | Frequency | 20 | 48.6 |  | Frequency | 30 | 48.4 |  | Frequency | 40 | 48.2 |  | Frequency | 50 | 50
1059 | TRUE | TRUE | DCC_LFDD_P05 | 1.0651 | 0.5 | No P(f) | Default | 0 | Default | 10 | 10 | Default | 60 | Frequency | 0 | 48.9 |  | Frequency | 10 | 48.8 |  | Frequency | 20 | 48.6 |  | Frequency | 30 | 48.4 |  | Frequency | 40 | 48.2 |  | Frequency | 50 | 50
1060 | TRUE | TRUE | DCC_LFDD+Fault | 1.0651 | 1 | No P(f) | Default | 0 | Default | 10 | 10 | Default | 20 | 3p fault | 0 | 40% | 0.45 | Frequency | 1 | 48.6 |  | Frequency | 10 | 50
1061 | TRUE | TRUE | DCC_Faera-O | 1.0651 | 1 | No P(f) | Default | 0 | Default | 10 | 10 | Default | 60 | Frequency | 0 | 50.5 |  | Frequency | 10 | 51 |  | Frequency | 20 | 51.5 |  | Frequency | 30 | 52 |  | Frequency | 40 | 53 |  | Frequency | 50 | 50
1062 | TRUE | TRUE | DCC_Faera-U | 1.0651 | 1 | No P(f) | Default | 0 | Default | 10 | 10 | Default | 70 | Frequency | 0 | 49.5 |  | Frequency | 10 | 49 |  | Frequency | 20 | 48 |  | Frequency | 30 | 47.5 |  | Frequency | 40 | 47 |  | Frequency | 50 | 46.5 |  | Frequency | 60 | 50
1063 | TRUE | TRUE | DCC_Uarea_Qreq_1(up) | 1.0651 | 1 | No P(f) | Default | 0 | Default | -1 | 0 | Default | 50 | Voltage | 0 | 1.118
1064 | TRUE | TRUE | DCC_Uarea_Qreq_2(up) | 1.118 | 1 | No P(f) | Default | 0 | Default | -1 | 0 | Default | 50 | Voltage | 0 | 1.15
1065 | TRUE | TRUE | DCC_Uarea_Qreq_1(down) | 1.0651 | 1 | No P(f) | Default | 0 | Default | -1 | 0 | Default | 50 | Voltage | 0 | 0.9
1066 | TRUE | TRUE | DCC_Uarea_Qreq_2(down) | 1 | 1 | No P(f) | Default | 0 | Default | -1 | 0 | Default | 50 | Voltage | 0 | 0.95
1067 | TRUE | TRUE | DCC_Uarea_Qreq_3(down) | 0.95 | 1 | No P(f) | Default | 0 | Default | -1 | 0 | Default | 50 | Voltage | 0 | 0.9
1068 | TRUE | TRUE | DCC_Uarea_ramp_up | 1.0651 | 1 | No P(f) | Default | 0 | Default | 10 | 10 | Default | 60 | dVoltage | 0 |  | 0.005 | dVoltage | 10 |  | 0 | dVoltage | 30 |  | -0.005 | dVoltage | 40 |  | 0
1069 | TRUE | TRUE | DCC_Uarea_ramp_down | 1.0651 | 1 | No P(f) | Default | 0 | Default | 10 | 10 | Default | 60 | dVoltage | 0 | 0 | -0.005 | dVoltage | 10 | -0.05 | 0 | dVoltage | 30 | -0.05 | 0.005 | dVoltage | 40 | 0 | 0
1070 | TRUE | TRUE | DCC_Overvoltage_characteristic | 1.0651 | 1 | No P(f) | Default | 0 | Default | -1 | 0 | Default | 30 | Voltage | 0 | 1.15 | 0 | Voltage | 10 | 1.2 | 0 | Voltage | 17 | 1.3 | 0 | Voltage | 25 | 1.0651
1071 | TRUE | TRUE | DCC_Undervoltage_characteristic | 1.0651 | 1 | No P(f) | Default | 0 | Default | -1 | 0 | Default | 45 | Voltage | 0 | 0.9 |  | Voltage | 10 | 0.85 |  | Voltage | 17 | 0.8 |  | Voltage | 25 | 0.7 |  | Voltage | 32 | 0.6 |  | Voltage | 37 | 1.0651
1072 | TRUE | TRUE | DCC_VoltageRise_insta_min | 1.0651 | 1 | No P(f) | Default | 0 | Default | 10 | 10 | Default | 20 | dVoltage | 0 | 0.3 | 0 | dVoltage | 0.1 | 0 |  | dVoltage | 3 | 0.5 |  | dVoltage | 3.1 | 0 |  | dVoltage | 6 | 0.7 |  | dVoltage | 6.1 | 0 |  | dVoltage | 9 | 0.9 |  | dVoltage | 9.1 | 0 |  | dVoltage | 12 | 1.1 |  | dVoltage | 12.1 | 0 |  | dVoltage | 15 | 1.3 |  | dVoltage | 15.1 | 0
1073 | TRUE | TRUE | DCC_VoltageRise_insta_max | 1.0651 | 1 | No P(f) | Default | 0 | Default | 30 | 10 | Default | 20 | dVoltage | 0 | 0.3 | 0 | dVoltage | 0.1 | 0 |  | dVoltage | 3 | 0.5 |  | dVoltage | 3.1 | 0 |  | dVoltage | 6 | 0.7 |  | dVoltage | 6.1 | 0 |  | dVoltage | 9 | 0.9 |  | dVoltage | 9.1 | 0 |  | dVoltage | 12 | 1.1 |  | dVoltage | 12.1 | 0 |  | dVoltage | 15 | 1.3 |  | dVoltage | 15.1 | 0
1074 | TRUE | TRUE | DCC_VoltageDip_insta_min | 1.0651 | 1 | No P(f) | Default | 0 | Default | 10 | 10 | Default | 20 | dVoltage | 0 | -0.1 | 0 | dVoltage | 0.1 | 0 |  | dVoltage | 3 | -0.15 |  | dVoltage | 3.1 | 0 |  | dVoltage | 6 | -0.2 |  | dVoltage | 6.1 | 0 |  | dVoltage | 9 | -0.25 |  | dVoltage | 9.1 | 0 |  | dVoltage | 12 | -0.3 |  | dVoltage | 12.1 | 0 |  | dVoltage | 15 | -0.35 |  | dVoltage | 15.1 | 0
1075 | TRUE | TRUE | DCC_VoltageDip_insta_max | 1.0651 | 1 | No P(f) | Default | 0 | Default | 30 | 10 | Default | 20 | dVoltage | 0 | -0.1 | 0 | dVoltage | 0.1 | 0 |  | dVoltage | 3 | -0.15 |  | dVoltage | 3.1 | 0 |  | dVoltage | 6 | -0.2 |  | dVoltage | 6.1 | 0 |  | dVoltage | 9 | -0.25 |  | dVoltage | 9.1 | 0 |  | dVoltage | 12 | -0.3 |  | dVoltage | 12.1 | 0 |  | dVoltage | 15 | -0.35 |  | dVoltage | 15.1 | 0
1076 | TRUE | TRUE | DCC_freqRise_insta_Source | 1.0651 | 1 | No P(f) | Default | 0 | Default | -1 | 0 | Default | 20 | Frequency | 0 | 52 | 0 | Frequency | 0.1 | 50 |  | Frequency | 3 | 52.5 |  | Frequency | 3.1 | 50 |  | Frequency | 6 | 53 |  | Frequency | 6.1 | 50 |  | Frequency | 9 | 55 |  | Frequency | 9.1 | 50 |  | Frequency | 12 | 60 |  | Frequency | 12.1 | 50 |  | Frequency | 15 | 65 |  | Frequency | 15.1 | 50
1077 | TRUE | TRUE | DCC_freqDip_insta_Source | 1.0651 | 1 | No P(f) | Default | 0 | Default | -1 | 0 | Default | 15 | Frequency | 0 | 47.5 | 0 | Frequency | 0.1 | 50 |  | Frequency | 3 | 47 |  | Frequency | 3.1 | 50 |  | Frequency | 6 | 46.5 |  | Frequency | 6.1 | 50 |  | Frequency | 9 | 46 |  | Frequency | 9.1 | 50
1078 | TRUE | TRUE | DCC_proc_VoltageRise_1.2 | 1 | 1 | No P(f) | Default | 0 | Default | 10 | 10 | Default | 60 | dVoltage | 0 | 0.2 | 0
1079 | TRUE | TRUE | DCC_proc_VoltageRise_1.3 | 1 | 1 | No P(f) | Default | 0 | Default | 10 | 10 | Default | 60 | dVoltage | 0 | 0.3 | 0
1080 | TRUE | TRUE | DCC_proc_VoltageRise_1.4 | 1 | 1 | No P(f) | Default | 0 | Default | 10 | 10 | Default | 60 | dVoltage | 0 | 0.4 | 0
1081 | TRUE | TRUE | DCC_proc_VoltageRise_1.5 | 1 | 1 | No P(f) | Default | 0 | Default | 10 | 10 | Default | 60 | dVoltage | 0 | 0.5 | 0
1082 | TRUE | TRUE | DCC_proc_Fault_3_0.8pu | 1.0651 | 1 | No P(f) | Default | 0 | Default | 10 | 10 | Default | 60 | 3p fault | 0 | 80% | 60
1083 | TRUE | TRUE | DCC_proc_Fault_3_0.6pu | 1.0651 | 1 | No P(f) | Default | 0 | Default | 10 | 10 | Default | 60 | 3p fault | 0 | 60% | 60
1084 | TRUE | TRUE | DCC_proc_Fault_3_0.40pu | 1.0651 | 1 | No P(f) | Default | 0 | Default | 10 | 10 | Default | 60 | 3p fault | 0 | 40% | 60
1085 | TRUE | TRUE | DCC_proc_Fault_3_0.20pu | 1.0651 | 1 | No P(f) | Default | 0 | Default | 10 | 10 | Default | 60 | 3p fault | 0 | 20% | 60
1086 | TRUE | TRUE | DCC_proc_Fault_1_0.05pu | 1.0651 | 1 | No P(f) | Default | 0 | Default | 30 | 10 | Default | 60 | 1p fault | 0 | 5% | 60

## Unit cases
Case |  |  |  | Initial Settings | [10 empty] | Event 1 |  |  |  | Event 2 |  |  |  | Event 3 |  |  |  | Event 4 |  |  |  | Event 5 |  |  |  | Event 6 |  |  |  | Event 7 |  |  |  | Event 8 |  |  |  | Event 9 |  |  |  | Event 10 |  |  |  | Event 11 |  |  |  | Event 12
Rank | RMS | EMT | Name | U0 | P0 | Pavail0 | Pmode | Qmode | Qref0 | QUdroop0 | SCR0 | XR0 | MtrfrGnd0 | Simulationtime | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2
2001 | TRUE | TRUE | UNT_SS_flatrun_Q1 | 1.0651 | 0 | Default | No P(f) | Default | 0 | Default | 10 | 10 | Default | 60 | PF disconnect all ref.
2002 | TRUE | TRUE | UNT_SS_flatrun_Q2 | 1.0651 | 0.5 | Default | No P(f) | Default | 0.2 | Default | 10 | 10 | Default | 60 | PF disconnect all ref.
2003 | TRUE | TRUE | UNT_SS_flatrun_Q3 | 1.0651 | 0.5 | Default | No P(f) | Default | -0.2 | Default | 10 | 10 | Default | 60 | PF disconnect all ref.
2004 | TRUE | TRUE | UNT_SS_flatrun_Q4 | 1.0651 | 1 | Default | No P(f) | Default | 0.33 | Default | 10 | 10 | Default | 60 | PF disconnect all ref.
2005 | TRUE | TRUE | UNT_SS_flatrun_Q5 | 1.0651 | 1 | Default | No P(f) | Default | -0.33 | Default | 10 | 10 | Default | 60 | PF disconnect all ref.
2006 | TRUE | TRUE | UNT_SS_flatrun_Q6 | 1.0651 | 1 | Default | No P(f) | Default | 0 | Default | 10 | 10 | Default | 60 | PF disconnect all ref.
2007 | TRUE | TRUE | UNT_P_step_up_0.5_0.7 | 1.0651 | 0.5 | Default | No P(f) | Default | 0 | Default | 10 | 10 | Default | 20 | Pref | 0 | 0.7 | 0 | Pref | 10 | 0.5
2008 | TRUE | TRUE | UNT_Q_control_up | 1.0651 | 1 | Default | No P(f) | Default | 0 | Default | 10 | 10 | Default | 20 | Qref | 0 | 0.1 |  | Qref | 5 | 0.2 |  | Qref | 10 | -0.1 |  | Qref | 15 | 0
2009 | TRUE | TRUE | UNT_U-Q/Pn_Neutral | 1.0651 | 1 | Default | No P(f) | Default | 0 | Default | -1 | 0 | Default | 20 | Voltage | 0 | 1.118 |  | Voltage | 5 | 1.0651 |  | Voltage | 10 | 0.968 |  | Voltage | 15 | 1.0651
2010 | TRUE | TRUE | Unit_Uarea_Qreq_1(up) | 1.0651 | 1 | Default | No P(f) | Default | 1.0651 | Default | -1 | 0 | Default | 50 | Voltage | 0 | 1.118
2011 | TRUE | TRUE | Unit_Uarea_Qreq_2(up) | 1.118 | 1 | Default | No P(f) | Default | 1.0651 | Default | -1 | 0 | Default | 50 | Voltage | 0 | 1.15
2012 | TRUE | TRUE | Unit_Uarea_Qreq_1(down) | 1.0651 | 1 | Default | No P(f) | Default | 1.0651 | Default | -1 | 0 | Default | 50 | Voltage | 0 | 0.96513
2013 | TRUE | TRUE | Unit_Uarea_Qreq_2(down) | 1 | 1 | Default | No P(f) | Default | 1 | Default | -1 | 0 | Default | 50 | Voltage | 0 | 0.95
2014 | TRUE | TRUE | Unit_Uarea_Qreq_3(down) | 0.95 | 1 | Default | No P(f) | Default | 1.0651 | Default | -1 | 0 | Default | 50 | Voltage | 0 | 0.9
2015 | TRUE | TRUE | UNT_Uarea_ramp_up | 1.0651 | 1 | Default | No P(f) | Default | 1.0651 | Default | 10 | 10 | Default | 60 | dVoltage | 0 |  | 0.005 | dVoltage | 10 |  | 0 | dVoltage | 30 |  | -0.005 | dVoltage | 40 |  | 0
2016 | TRUE | TRUE | UNT_Uarea_ramp_down | 1.0651 | 1 | Default | No P(f) | Default | 1.0651 | Default | 10 | 10 | Default | 60 | dVoltage | 0 |  | -0.005 | dVoltage | 10 |  | 0 | dVoltage | 30 |  | 0.005 | dVoltage | 40 |  | 0
2017 | TRUE | TRUE | UNT_fArea | 1.0651 | 0.7 | Default | No P(f) | Default | 0 | Default | 10 | 10 | Default | 100 | Frequency | 0 | 51.5 |  | Frequency | 20 | 50 |  | Frequency | 40 | 48.5 |  | Frequency | 60 | 47.5 |  | Frequency | 80 | 50
2018 | TRUE | TRUE | UNT_LVFRT_profile | 1.0651 | 1 | Default | No P(f) | Default | 0 | Default | -1 | 0 | Default | 20 | Voltage | 0 | 0 | 0 | Voltage | 0.1498 | 0 | 0 | Voltage | 0.1499 | 0 | 0 | Voltage | 0.15 | 0 | 0.62963 | Voltage | 1.5 | 0.85 | 0
2019 | TRUE | TRUE | UNT_OVRT_profile | 1.0651 | 1 | Default | No P(f) | Default | 0 | Default | -1 | 0 | Default | 50 | Voltage | 0 | 1.3 |  | Voltage | 0.1 | 1.2 |  | Voltage | 30 | 1.15
2020 | TRUE | TRUE | UNT_Fault_3_0 | 1.0651 | 1 | Default | No P(f) | Default | 0 | Default | 10 | 10 | Default | 12 | 3p fault | 0 | 0% | 0.15
2021 | TRUE | TRUE | UNT_Fault_3_20 | 1.0651 | 1 | Default | No P(f) | Default | 0 | Default | 10 | 10 | Default | 12 | 3p fault | 0 | 20% | 0.45
2022 | TRUE | TRUE | UNT_Fault_3_40 | 1.0651 | 1 | Default | No P(f) | Default | 0 | Default | 10 | 10 | Default | 12 | 3p fault | 0 | 40% | 0.75
2023 | TRUE | TRUE | UNT_Fault_3_80 | 1.0651 | 1 | Default | No P(f) | Default | 0 | Default | 10 | 10 | Default | 12 | 3p fault | 0 | 80% | 1.35
2024 | TRUE | TRUE | UNT_Fault_2_0 | 1.0651 | 1 | Default | No P(f) | Default | 0 | Default | 10 | 10 | Default | 12 | 2p-g fault | 0 | 0% | 0.15
2025 | TRUE | TRUE | UNT_Fault_2_20 | 1.0651 | 1 | Default | No P(f) | Default | 0 | Default | 10 | 10 | Default | 12 | 2p-g fault | 0 | 20% | 0.45
2026 | TRUE | TRUE | UNT_Fault_2_40 | 1.0651 | 1 | Default | No P(f) | Default | 0 | Default | 10 | 10 | Default | 12 | 2p-g fault | 0 | 40% | 0.75
2027 | TRUE | TRUE | UNT_Fault_2_80 | 1.0651 | 1 | Default | No P(f) | Default | 0 | Default | 10 | 10 | Default | 12 | 2p-g fault | 0 | 80% | 1.35
2028 | TRUE | TRUE | UNT_Fault_1_0 | 1.0651 | 1 | Default | No P(f) | Default | 0 | Default | 10 | 10 | Default | 12 | 1p fault | 0 | 0% | 0.15
2029 | TRUE | TRUE | UNT_Fault_1_20 | 1.0651 | 1 | Default | No P(f) | Default | 0 | Default | 10 | 10 | Default | 12 | 1p fault | 0 | 20% | 0.45
2030 | TRUE | TRUE | UNT_Fault_1_40 | 1.0651 | 1 | Default | No P(f) | Default | 0 | Default | 10 | 10 | Default | 12 | 1p fault | 0 | 40% | 0.75
2031 | TRUE | TRUE | UNT_Fault_1_80 | 1.0651 | 1 | Default | No P(f) | Default | 0 | Default | 10 | 10 | Default | 12 | 1p fault | 0 | 80% | 1.35
2032 | TRUE | TRUE | UNT_Voltage-support | 1.0651 | 1 | Default | No P(f) | Default | 0 | Default | -1 | 0 | Default | 5 | Voltage | 0 | 70% |  | Voltage | 0.2 | 0.5 |  | Voltage | 0.4 | 0.3 |  | Voltage | 0.6 | 1
2033 | TRUE | TRUE | UNT_Fault_1_restrike | 1.0651 | 1 | Default | No P(f) | Default | 0 | Default | 10 | 10 | Default | 15 | 1p fault | 0 | 5% | 0.15 | 1p fault | 1.35 | 5% | 0.15 | 1p fault | 3 | 20% | 0.15 | 1p fault | 3.45 | 20% | 0.15
2034 | TRUE | TRUE | UNT_Fault_3_double | 1.0651 | 1 | Default | No P(f) | Default | 0 | Default | 10 | 10 | Default | 15 | 3p fault | 0 | 10% | 0.15 | 3p fault | 1.65 | 20% | 0.15
2035 | TRUE | TRUE | UNT_Fault_2_double | 1.0651 | 1 | Default | No P(f) | Default | 0 | Default | 10 | 10 | Default | 15 | 2p fault | 0 | 10% | 0.15 | 2p-g fault | 1.65 | 20% | 0.15
2036 | TRUE | TRUE | UNT_Fault_3_20_short | 1.0651 | 1 | Default | No P(f) | Default | 0 | Default | 10 | 10 | Default | 2 | 3p fault | 0 | 20% | 0.25 | SCR | 0.249 | 10 | 10
2037 | TRUE | TRUE | UNT_Fault_2_20_short | 1.0651 | 1 | Default | No P(f) | Default | 0 | Default | 10 | 10 | Default | 2 | 2p-g fault | 0 | 20% | 0.25
2038 | TRUE | TRUE | UNT_Fault_3_20_WG | 1.0651 | 1 | Default | No P(f) | Default | 0 | Default | 2 | 3 | Default | 12 | 3p fault | 0 | 20% | 0.2
2039 | TRUE | TRUE | UNT_Fault_2_20_WG | 1.0651 | 1 | Default | No P(f) | Default | 0 | Default | 2 | 3 | Default | 12 | 2p-g fault | 0 | 20% | 0.2
2040 | TRUE | TRUE | UNT_Fault_3_SCR | 1.0651 | 1 | Default | No P(f) | Default | 0 | Default | 20 | 15 | Default | 12 | 3p fault | 0 | 5% | 0.15 | SCR | 0.149 | 10 | 10
2041 | TRUE | TRUE | UNT_Fault_2_SCR | 1.0651 | 1 | Default | No P(f) | Default | 0 | Default | 20 | 15 | Default | 12 | 2p fault | 0 | 10% | 0.15 | SCR | 0.149 | 10 | 10
2042 | TRUE | TRUE | UNT_Fault_rec_1_Q | 1.0651 | 1 | Default | No P(f) | Default | 1.0651 | Default | -1 | 0 | Default |  | Voltage recording |  | recordings/DK1_fault1.csv | 1.0651
2043 | TRUE | TRUE | UNT_Fault_rec_3_Q | 1.0651 | 1 | Default | No P(f) | Default | 1.0651 | Default | -1 | 0 | Default |  | Voltage recording |  | recordings/slow_recovery.csv | 1.0651
2044 | TRUE | TRUE | UNT_Fault_3_SCR_freqStep | 1.0651 | 1 | Default | No P(f) | Default | 0 | Default | 20 | 15 | Default | 12 | 3p fault | 0 | 40% | 0.2 | SCR | 0.199 | 10 | 10 | Frequency | 0.205 | 51 |  | Frequency | 5.5 | 50
2045 | TRUE | TRUE | Unit_SCR_step_Max-Min | 1.0651 | 1 | Default | No P(f) | Default | 0 | Default | 30 | 20 | Default | 10 | SCR | 0 | 10 | 10 | SCR | 5 | 30 | 20
2046 | TRUE | TRUE | UNT_FRTsensitivity | 1 | 1 | Default | No P(f) | Default | 1 | Default | -1 | 0 | Default | 85 | Voltage | 2 | 0.85 |  | Voltage | 8 | 1 |  | Voltage | 20 | 0.84 |  | Voltage | 26 | 1 |  | Voltage | 40 | 0.86 |  | Voltage | 46 | 0.8 |  | Voltage | 51 | 1 |  | Voltage | 65 | 0.86 |  | Voltage | 71 | 0.75 |  | Voltage | 73 | 1
2047 | TRUE | TRUE | UNT_FRTsensitivity-ramp | 1 | 1 | Default | No P(f) | Default | 1 | Default | -1 | 0 | Default | 20 | dVoltage | 2 |  | -0.05 | dVoltage | 5.4 |  | 0 | dVoltage | 10.4 |  | 0.1 | dVoltage | 12.1 |  | 0
2048 | TRUE | TRUE | UNT_MaxPhaseJump | 1.0651 | 1 | Default | No P(f) | Default | 0 | Default | 10 | 10 | Default | 10 | Phase | 0 | 20 |  | Phase | 2.5 | 0 |  | Phase | 5 | -20 |  | Phase | 7.5 | 0
2049 | TRUE | TRUE | UNT_MaxPhaseJump2 | 1.0651 | 1 | Default | No P(f) | Default | 0 | Default | 10 | 10 | Default | 5 | Phase | 0 | 6.5 |  | Phase | 0.02 | 13.25 |  | Phase | 0.04 | 20 |  | Phase | 2.5 | 13.5 |  | Phase | 2.52 | 6.75 |  | Phase | 2.54 | 0
2050 | TRUE | TRUE | UNT_MaxRoCoF1 | 1.0651 | 1 | Default | No P(f) | Default | 1.0651 | Default | 10 | 10 | Default | 10 | Frequency | 0 | 50 | 2 | Frequency | 0.5 |  | -2 | Frequency | 1 |  | 0 | Frequency | 2 | 50 | -0.5 | Frequency | 4 |  | 0.5 | Frequency | 6 |  | 0
2051 | TRUE | TRUE | UNT_MaxRoCoF2 | 1.0651 | 1 | Default | No P(f) | Default | 1.0651 | Default | 10 | 10 | Default | 5 | Frequency | 0 | 50 | -4 | Frequency | 0.08 |  | 0 | Frequency | 0.1 |  | 4 | Frequency | 0.2 | 50 | 0 | Frequency | 0.22 |  | 4 | Frequency | 0.3 |  | 0 | Frequency | 0.32 |  | -4 | Frequency | 0.42 |  | 0 | Frequency | 1 |  | -20 | Frequency | 1.02 |  | 0 | Frequency | 1.04 |  | 20 | Frequency | 1.06 |  | 0
2052 | TRUE | TRUE | UNT_MaxRoCoF_CurveOF | 1.0651 | 0.7 | Default | No P(f) | Default | 0 | Default | 10 | 10 | Default | 10 | Frequency | 0 |  | 4 | Frequency | 0.05 |  | 2 | Frequency | 0.15 |  | 1 | Frequency | 0.9 |  | 0.35 | Frequency | 1.9 |  | 0 | Frequency | 3.9 |  | -1 | Frequency | 4.9 |  | 0
2053 | TRUE | TRUE | UNT_MaxRoCoF_CurveUF | 1.0651 | 0.7 | Default | No P(f) | Default | 0 | Default | 10 | 10 | Default | 10 | Frequency | 0 |  | -4 | Frequency | 0.05 |  | -2 | Frequency | 0.15 |  | -1 | Frequency | 0.9 |  | -0.35 | Frequency | 1.9 |  | 0 | Frequency | 3.9 |  | 1 | Frequency | 4.9 |  | 0
2054 | TRUE | TRUE | UNT_MaxPhaseJump_Extreme_min | 1.0651 | 1 | Default | No P(f) | Default | 0 | Default | 10 | 10 | Default | 30 | Phase | 0 | 30 |  | Phase | 2.5 | 0 |  | Phase | 5 | 40 |  | Phase | 7.5 | 0 |  | Phase | 10 | 50 |  | Phase | 12.5 | 0 |  | Phase | 15 | 60 |  | Phase | 17.5 | 0 |  | Phase | 20 | 70 |  | Phase | 22.5 | 0
2055 | TRUE | TRUE | UNT_MaxPhaseJump_Extreme_max | 1.0651 | 1 | Default | No P(f) | Default | 0 | Default | 30 | 20 | Default | 30 | Phase | 0 | 30 |  | Phase | 2.5 | 0 |  | Phase | 5 | 40 |  | Phase | 7.5 | 0 |  | Phase | 10 | 50 |  | Phase | 12.5 | 0 |  | Phase | 15 | 60 |  | Phase | 17.5 | 0 |  | Phase | 20 | 70 |  | Phase | 22.5 | 0
2056 | TRUE | TRUE | UNT_Overvoltage_characteristic | 1.0651 | 1 | Default | No P(f) | Default | 1.0651 | Default | -1 | 0 | Default | 30 | Voltage | 0 | 1.15 | 0 | Voltage | 10 | 1.2 | 0 | Voltage | 17 | 1.3 | 0 | Voltage | 25 | 1
2057 | TRUE | TRUE | UNT_Undervoltage_characteristic | 1.0651 | 1 | Default | No P(f) | Default | 1.0651 | Default | -1 | 0 | Default | 45 | Voltage | 0 | 0.9 |  | Voltage | 10 | 0.85 |  | Voltage | 17 | 0.8 |  | Voltage | 25 | 0.7 |  | Voltage | 32 | 0.6 |  | Voltage | 37 | 1
2058 | TRUE | TRUE | UNT_VoltageRise_1.2 | 1 | 1 | Default | No P(f) | Default | 0 | Default | 10 | 10 | Default | 60 | dVoltage | 0 | 0.2 | 0
2059 | TRUE | TRUE | UNT_VoltageRise_1.3 | 1 | 1 | Default | No P(f) | Default | 0 | Default | 10 | 10 | Default | 60 | dVoltage | 0 | 0.3 | 0
2060 | TRUE | TRUE | UNT_VoltageRise_1.4 | 1 | 1 | Default | No P(f) | Default | 0 | Default | 10 | 10 | Default | 60 | dVoltage | 0 | 0.4 | 0
2061 | TRUE | TRUE | UNT_VoltageRise_1.5 | 1 | 1 | Default | No P(f) | Default | 0 | Default | 10 | 10 | Default | 60 | dVoltage | 0 | 0.5 | 0
2062 | TRUE | TRUE | UNT_VoltageRise_insta_min | 1 | 1 | Default | No P(f) | Default | 0 | Default | 10 | 10 | Default | 10 | Voltage | 0 | 1.3 | 0 | Voltage | 0.1 | 1 |  | Voltage | 1 | 1.5 |  | Voltage | 1.1 | 1 |  | Voltage | 2 | 1.7 |  | Voltage | 2.1 | 1 |  | Voltage | 3 | 1.9 |  | Voltage | 3.1 | 1 |  | Voltage | 4 | 2.1 |  | Voltage | 4.1 | 1 |  | Voltage | 5 | 2.3 |  | Voltage | 5.1 | 1
2063 | TRUE | TRUE | UNT_VoltageRise_insta_max | 1 | 1 | Default | No P(f) | Default | 0 | Default | 30 | 20 | Default | 10 | Voltage | 0 | 1.3 | 0 | Voltage | 0.1 | 1 |  | Voltage | 1 | 1.5 |  | Voltage | 1.1 | 1 |  | Voltage | 2 | 1.7 |  | Voltage | 2.1 | 1 |  | Voltage | 3 | 1.9 |  | Voltage | 3.1 | 1 |  | Voltage | 4 | 2.1 |  | Voltage | 4.1 | 1 |  | Voltage | 5 | 2.3 |  | Voltage | 5.1 | 1
2064 | TRUE | TRUE | UNT_VoltageDip_insta_min | 1 | 1 | Default | No P(f) | Default | 1 | Default | 10 | 10 | Default | 20 | dVoltage | 0 | -0.1 | 0 | dVoltage | 0.1 | 0 |  | dVoltage | 3 | -0.15 |  | dVoltage | 3.1 | 0 |  | dVoltage | 6 | -0.2 |  | dVoltage | 6.1 | 0 |  | dVoltage | 9 | -0.25 |  | dVoltage | 9.1 | 0 |  | dVoltage | 12 | -0.3 |  | dVoltage | 12.1 | 0
2065 | TRUE | TRUE | UNT_VoltageDip_insta_max | 1 | 1 | Default | No P(f) | Default | 1 | Default | 30 | 20 | Default | 20 | dVoltage | 0 | -0.1 | 0 | dVoltage | 0.1 | 0 |  | dVoltage | 3 | -0.15 |  | dVoltage | 3.1 | 0 |  | dVoltage | 6 | -0.2 |  | dVoltage | 6.1 | 0 |  | dVoltage | 9 | -0.25 |  | dVoltage | 9.1 | 0 |  | dVoltage | 12 | -0.3 |  | dVoltage | 12.1 | 0
2066 | TRUE | TRUE | Unit_freqRise_insta_min | 1 | 1 | Default | No P(f) | Default | 0 | Default | 10 | 10 | Default | 10 | Frequency | 0 | 52 | 0 | Frequency | 0.05 | 50 |  | Frequency | 1 | 52.5 |  | Frequency | 1.05 | 50 |  | Frequency | 2 | 53 |  | Frequency | 2.05 | 50 |  | Frequency | 3 | 55 |  | Frequency | 3.05 | 50 |  | Frequency | 4 | 60 |  | Frequency | 4.05 | 50 |  | Frequency | 5 | 65 |  | Frequency | 5.05 | 50
2067 | TRUE | TRUE | Unit_freqDip_insta_min | 1 | 1 | Default | No P(f) | Default | 0 | Default | 10 | 10 | Default | 10 | Frequency | 0 | 47.5 | 0 | Frequency | 0.05 | 50 |  | Frequency | 1 | 47 |  | Frequency | 1.05 | 50 |  | Frequency | 2 | 46.5 |  | Frequency | 2.05 | 50 |  | Frequency | 3 | 46 |  | Frequency | 3.05 | 50
2068 | TRUE | TRUE | UNT_prot_Fault_3_0.8pu | 1 | 1 | Default | No P(f) | Default | 0 | Default | 10 | 10 | Default | 60 | 3p fault | 0 | 80% | 60
2069 | TRUE | TRUE | UNT_prot_Fault_3_0.6pu | 1 | 1 | Default | No P(f) | Default | 0 | Default | 10 | 10 | Default | 60 | 3p fault | 0 | 60% | 60
2070 | TRUE | TRUE | UNT_prot_Fault_3_0.40pu | 1 | 1 | Default | No P(f) | Default | 0 | Default | 10 | 10 | Default | 60 | 3p fault | 0 | 40% | 60
2071 | TRUE | TRUE | UNT_prot_Fault_3_0.20pu | 1 | 1 | Default | No P(f) | Default | 0 | Default | 10 | 10 | Default | 60 | 3p fault | 0 | 20% | 60
2072 | TRUE | TRUE | UNT_prot_Fault_1_0.05pu | 1 | 1 | Default | No P(f) | Default | 0 | Default | 10 | 10 | Default | 60 | 1p fault | 0 | 5% | 60
2073 | TRUE | TRUE | UNT_Freq_53Hz | 1 | 0.7 | Default | No P(f) | Default | 0 | Default | 10 | 10 | Default | 60 | Frequency | 0 | 53
2074 | TRUE | TRUE | UNT_Freq_46Hz | 1 | 0.7 | Default | No P(f) | Default | 0 | Default | 10 | 10 | Default | 60 | Frequency | 0 | 46
2075 | TRUE | TRUE | UNT_Freq_limit_up | 1 | 0.7 | Default | No P(f) | Default | 0 | Default | 10 | 10 | Default | 30 | Frequency | 0 | 52 |  | Frequency | 5 | 53 |  | Frequency | 10 | 54 |  | Frequency | 15 | 55 |  | Frequency | 20 | 56 |  | Frequency | 25 | 50
2076 | TRUE | TRUE | UNT_Freq_limi_down | 1 | 0.7 | Default | No P(f) | Default | 0 | Default | 10 | 10 | Default | 30 | Frequency | 0 | 47 |  | Frequency | 5 | 46 |  | Frequency | 10 | 45 |  | Frequency | 15 | 44 |  | Frequency | 20 | 43 |  | Frequency | 25 | 50
2077 | FALSE | TRUE | UNT_Pavail_variation | 1.0651 | 1 | Default | No P(f) | Default | 0 | Default | 10 | 10 | Default | 20 | Signal 2 | 1 | 0.75 |  | Signal 2 | 5 | 0.25 |  | Signal 2 | 10 | 1

## Co-located cases
Case |  |  |  | Initial Settings | [16 empty] | Event 1 |  |  |  | Event 2 |  |  |  | Event 3 |  |  |  | Event 4 |  |  |  | Event 5 |  |  |  | Event 6 |  |  |  | Event 7 |  |  |  | Event 8 |  |  |  | Event 9 |  |  |  | Event 10 |  |  |  | Event 11 |  |  |  | Event 12 |  |  |  | Event 13
Rank | RMS | EMT | Name | U0 | P0_unitA | Pavail0_unitA | P0_unitB | Pavail0_unitB | P0_unitC | Pavail0_unitC | P0_unitD | Pavail0_unitD | Pmode | Qmode | Qref0 | QUdroop0 | SCR0 | XR0 | MtrfrGnd0 | Simulationtime | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2
Note: Functionality for events and initial settings related to co-located facilities is not yet implemented.
To be constructed
Refer to testcases.xlsx tab 'Co-located cases overview' for guidance
- This textbox can be deleted.

## Custom cases
Case |  |  |  | Initial Settings | [10 empty] | Event 1 |  |  |  | Event 2 |  |  |  | Event 3 |  |  |  | Event 4 |  |  |  | Event 5 |  |  |  | Event 6 |  |  |  | Event 7 |  |  |  | Event 8 |  |  |  | Event 9 |  |  |  | Event 10 |  |  |  | Event 11 |  |  |  | Event 12
Rank | RMS | EMT | Name | U0 | P0 | Pavail0 | Pmode | Qmode | Qref0 | QUdroop0 | SCR0 | XR0 | MtrfrGnd0 | Simulationtime | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2
4001 | TRUE | TRUE | Custom_RfG_MaxFacilityCurrent | 0.86 | 1 | Default | LFSM | Q | 0.33 | Default | 10 | 10 | Default | 12 | PF disconnect all ref. | 0
4002 | TRUE | TRUE | Custom_RfG_Fault_3_FRTtrig_0.87pu | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 3p fault | 0 | 87% | 1
4003 | TRUE | TRUE | Custom_RfG_Fault_3_FRTtrig_0.86pu | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 3p fault | 0 | 86% | 1
4004 | TRUE | TRUE | Custom_RfG_Fault_3_FRTtrig_0.85pu | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 3p fault | 0 | 85% | 1
4005 | TRUE | TRUE | Custom_RfG_Fault_3_FRTtrig_0.84pu | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 3p fault | 0 | 84% | 1
4006 | TRUE | TRUE | Custom_RfG_Fault_3_FRTtrig_0.83pu | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 3p fault | 0 | 83% | 1
4007 | TRUE | TRUE | Custom_RfG_Fault_3_FRTtrig_0.82pu | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 3p fault | 0 | 82% | 1
4008 | TRUE | TRUE | Custom_RfG_Fault_3_FRTtrig_0.81pu | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 3p fault | 0 | 81% | 1
4009 | TRUE | TRUE | Custom_RfG_Fault_3_FRTtrig_0.80pu | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 3p fault | 0 | 80% | 1
4010 | TRUE | TRUE | Custom_RfG_Fault_3_FRTtrig_0.79pu | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 3p fault | 0 | 79% | 1
4011 | TRUE | TRUE | Custom_RfG_Fault_3_FRTtrig_0.78pu | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 3p fault | 0 | 78% | 1
4012 | TRUE | TRUE | Custom_RfG_LVRT_FRTexit_0.84pu | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | -1 | 0 | Default | 12 | Voltage | 0 | 0 | 0 | Voltage | 0.1498 | 0 | 0 | Voltage | 0.1499 | 0 | 0 | Voltage | 0.15 | 0 | 0.62222 | Voltage | 1.5 | 0.84 | 0
4013 | TRUE | TRUE | Custom_RfG_LVRT_FRTexit_0.85pu | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | -1 | 0 | Default | 12 | Voltage | 0 | 0 | 0 | Voltage | 0.1498 | 0 | 0 | Voltage | 0.1499 | 0 | 0 | Voltage | 0.15 | 0 | 0.62963 | Voltage | 1.5 | 0.85 | 0
4014 | TRUE | TRUE | Custom_RfG_LVRT_FRTexit_0.86pu | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | -1 | 0 | Default | 12 | Voltage | 0 | 0 | 0 | Voltage | 0.1498 | 0 | 0 | Voltage | 0.1499 | 0 | 0 | Voltage | 0.15 | 0 | 0.63704 | Voltage | 1.5 | 0.86 | 0
4015 | TRUE | TRUE | Custom_RfG_LVRT_FRTexit_0.87pu | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | -1 | 0 | Default | 12 | Voltage | 0 | 0 | 0 | Voltage | 0.1498 | 0 | 0 | Voltage | 0.1499 | 0 | 0 | Voltage | 0.15 | 0 | 0.64444 | Voltage | 1.5 | 0.87 | 0
4016 | TRUE | TRUE | Custom_RfG_LVRT_FRTexit_0.88pu | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | -1 | 0 | Default | 12 | Voltage | 0 | 0 | 0 | Voltage | 0.1498 | 0 | 0 | Voltage | 0.1499 | 0 | 0 | Voltage | 0.15 | 0 | 0.65185 | Voltage | 1.5 | 0.88 | 0
4017 | TRUE | TRUE | Custom_RfG_LVRT_FRTexit_0.89pu | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | -1 | 0 | Default | 12 | Voltage | 0 | 0 | 0 | Voltage | 0.1498 | 0 | 0 | Voltage | 0.1499 | 0 | 0 | Voltage | 0.15 | 0 | 0.65926 | Voltage | 1.5 | 0.89 | 0
4018 | TRUE | TRUE | Custom_RfG_Fault_3_MaxIQ_0.24pu | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 3p fault | 0 | 24% | 0.15
4019 | TRUE | TRUE | Custom_RfG_Fault_3_MaxIQ_0.23pu | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 3p fault | 0 | 23% | 0.15
4020 | TRUE | TRUE | Custom_RfG_Fault_3_MaxIQ_0.22pu | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 3p fault | 0 | 22% | 0.15
4021 | TRUE | TRUE | Custom_RfG_Fault_3_MaxIQ_0.21pu | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 3p fault | 0 | 21% | 0.15
4022 | TRUE | TRUE | Custom_RfG_Fault_3_MaxIQ_0.20pu | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 3p fault | 0 | 20% | 0.15
4023 | TRUE | TRUE | Custom_RfG_Fault_3_MaxIQ_0.19pu | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 3p fault | 0 | 19% | 0.15
4024 | TRUE | TRUE | Custom_RfG_Fault_3_MaxIQ_0.18pu | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 3p fault | 0 | 18% | 0.15
4025 | TRUE | TRUE | Custom_RfG_Fault_3_MaxIQ_0.17pu | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 3p fault | 0 | 17% | 0.15
4026 | TRUE | TRUE | Custom_RfG_Fault_3_MaxIQ_0.16pu | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 3p fault | 0 | 16% | 0.15
4027 | TRUE | TRUE | Custom_RfG_Fault_3_MaxIQ_0.15pu | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 3p fault | 0 | 15% | 0.15
4028 | TRUE | TRUE | Custom_RfG_Fault_3_0.2pu_Plim_0.5pu | 1.0651 | 0.5 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 20 | Signal 2 | -1 | 0.5 |  | 3p fault | 0 | 20% | 0.45
4029 | TRUE | TRUE | Custom_RfG_Fault_2_0.2pu_Plim_0.5pu | 1.0651 | 0.5 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 20 | Signal 2 | -1 | 0.5 |  | 2p-g fault | 0 | 20% | 0.45
4030 | TRUE | TRUE | Custom_RfG_Fault_1_0.2pu_Plim_0.5pu | 1.0651 | 0.5 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 20 | Signal 2 | -1 | 0.5 |  | 1p fault | 0 | 20% | 0.45
4031 | TRUE | TRUE | Custom_RfG_Fault_3_0.2pu_Plim_0.15pu | 1.0651 | 0.15 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 20 | Signal 2 | -1 | 0.15 |  | 3p fault | 0 | 20% | 0.45
4032 | TRUE | TRUE | Custom_RfG_Fault_2_0.2pu_Plim_0.15pu | 1.0651 | 0.15 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 20 | Signal 2 | -1 | 0.15 |  | 2p-g fault | 0 | 20% | 0.45
4033 | TRUE | TRUE | Custom_RfG_Fault_1_0.2pu_Plim_0.15pu | 1.0651 | 0.15 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 20 | Signal 2 | -1 | 0.15 |  | 1p fault | 0 | 20% | 0.45
4034 | TRUE | TRUE | Custom_RfG_Ucontrol_Plim_1.00pu | 1.0651 | 0.5 | Default | LFSM | Q(U) | 1.0651 | Default | 10 | 10 | Default | 25 | Signal 2 | -1 | 1 |  | dVoltage | 0 | 0.042605 |  | dVoltage | 7 | 0 |  | dVoltage | 14 | -0.042605 |  | dVoltage | 21 | 0
4035 | TRUE | TRUE | Custom_RfG_Ucontrol_Plim_0.50pu | 1.0651 | 0.5 | Default | LFSM | Q(U) | 1.0651 | Default | 10 | 10 | Default | 25 | Signal 2 | -1 | 0.5 |  | dVoltage | 0 | 0.042605 |  | dVoltage | 7 | 0 |  | dVoltage | 14 | -0.042605 |  | dVoltage | 21 | 0
4036 | TRUE | TRUE | Custom_RfG_Ucontrol_Plim_0.15pu | 1.0651 | 0.15 | Default | LFSM | Q(U) | 1.0651 | Default | 10 | 10 | Default | 25 | Signal 2 | -1 | 0.15 |  | dVoltage | 0 | 0.042605 |  | dVoltage | 7 | 0 |  | dVoltage | 14 | -0.042605 |  | dVoltage | 21 | 0
4037 | TRUE | TRUE | Custom_Fault_3_0.20pu_U0_1.118pu | 1.118 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 3p fault | 0 | 20% | 0.45
4038 | TRUE | TRUE | Custom_Fault_2_0.20pu_U0_1.118pu | 1.118 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 2p-g fault | 0 | 20% | 0.45
4039 | TRUE | TRUE | Custom_Fault_1_0.20pu_U0_1.118pu | 1.118 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 1p fault | 0 | 20% | 0.45
4040 | TRUE | TRUE | Custom_Fault_3_0.20pu_U0_0.968pu | 0.968 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 3p fault | 0 | 20% | 0.45
4041 | TRUE | TRUE | Custom_Fault_2_0.20pu_U0_0.968pu | 0.968 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 2p-g fault | 0 | 20% | 0.45
4042 | TRUE | TRUE | Custom_Fault_1_0.20pu_U0_0.968pu | 0.968 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 1p fault | 0 | 20% | 0.45
4043 | TRUE | TRUE | Custom_Fault_3_U0_1.118_Uend_1.065 | 1.118 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 3p fault | 0 | 20% | 0.45 | Voltage | 0.45 | 1.0651 | 0
4044 | TRUE | TRUE | Custom_Fault_2_U0_1.118_Uend_1.065 | 1.118 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 2p-g fault | 0 | 20% | 0.45 | Voltage | 0.45 | 1.0651 | 0
4045 | TRUE | TRUE | Custom_Fault_1_U0_1.118_Uend_1.065 | 1.118 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 1p fault | 0 | 20% | 0.45 | Voltage | 0.45 | 1.0651 | 0
4046 | TRUE | TRUE | Custom_Fault_3_U0_1.118_Uend_0.968 | 1.118 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 3p fault | 0 | 20% | 0.45 | Voltage | 0.45 | 0.968 | 0
4047 | TRUE | TRUE | Custom_Fault_3_U0_0.959_Uend_1.065 | 0.95862 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 3p fault | 0 | 20% | 0.45 | Voltage | 0.45 | 1.0651 | 0
4048 | TRUE | TRUE | Custom_Fault_2_U0_0.959_Uend_1.065 | 0.95862 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 2p-g fault | 0 | 20% | 0.45 | Voltage | 0.45 | 1.0651 | 0
4049 | TRUE | TRUE | Custom_Fault_1_U0_0.959_Uend_1.065 | 0.95862 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 1p fault | 0 | 20% | 0.45 | Voltage | 0.45 | 1.0651 | 0
4050 | TRUE | TRUE | Custom_Fault_3_U0_0.959_Uend_1.118 | 0.95862 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 3p fault | 0 | 20% | 0.45 | Voltage | 0.45 | 1.118 | 0
4051 | TRUE | TRUE | Custom_Fault_3_U0_1.118_Uend_0.900 | 1.118 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 3p fault | 0 | 20% | 0.45 | Voltage | 0.45 | 0.9 | 0
4052 | TRUE | TRUE | Custom_Fault_3_U0_1.065_Uend_0.900 | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 3p fault | 0 | 20% | 0.45 | Voltage | 0.45 | 0.9 | 0
4053 | TRUE | TRUE | Custom_Fault_3_U0_0.959_Uend_0.900 | 0.95862 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 3p fault | 0 | 20% | 0.45 | Voltage | 0.45 | 0.9 | 0
4054 | TRUE | TRUE | Custom_Fault_3_U0_1.065pu_OVRT_1.15 | 1.0651 | 1 | Default | LFSM | Q | 0 | Default | 10 | 10 | Default | 30 | 3p fault | 0 | 20% | 0.45 | Voltage | 0.45 | 1.15
4055 | TRUE | TRUE | Custom_Fault_3_U0_1.065pu_OVRT_1.20 | 1.0651 | 1 | Default | LFSM | Q | 0 | Default | 10 | 10 | Default | 30 | 3p fault | 0 | 20% | 0.45 | Voltage | 0.45 | 1.2 |  | Voltage | 20.45 | 1.15
4056 | TRUE | TRUE | Custom_Fault_3_U0_1.065pu_OVRT_1.30 | 1.0651 | 1 | Default | LFSM | Q | 0 | Default | 10 | 10 | Default | 30 | 3p fault | 0 | 20% | 0.45 | Voltage | 0.45 | 1.3 |  | Voltage | 0.55 | 1.2 |  | Voltage | 20.55 | 1.15
4057 | TRUE | TRUE | Custom_Fault_3_U0_1.065pu_OVRT_1.15 | 1.0651 | 1 | Default | LFSM | Q(U) | 0 | Default | 10 | 10 | Default | 30 | 3p fault | 0 | 20% | 0.45 | Voltage | 0.45 | 1.15
4058 | TRUE | TRUE | Custom_Fault_3_U0_1.065pu_OVRT_1.20 | 1.0651 | 1 | Default | LFSM | Q(U) | 0 | Default | 10 | 10 | Default | 30 | 3p fault | 0 | 20% | 0.45 | Voltage | 0.45 | 1.2 |  | Voltage | 20.45 | 1.15
4059 | TRUE | TRUE | Custom_Fault_3_U0_1.065pu_OVRT_1.30 | 1.0651 | 1 | Default | LFSM | Q(U) | 0 | Default | 10 | 10 | Default | 30 | 3p fault | 0 | 20% | 0.45 | Voltage | 0.45 | 1.3 |  | Voltage | 0.55 | 1.2 |  | Voltage | 20.55 | 1.15
4060 | TRUE | TRUE | Custom_Fault_3_0.20pu_SCR_2 | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 2 | 10 | Default | 12 | 3p fault | 0 | 20% | 0.45
4061 | TRUE | TRUE | Custom_Fault_3_0.20pu_SCR_3 | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 3 | 10 | Default | 12 | 3p fault | 0 | 20% | 0.45
4062 | TRUE | TRUE | Custom_Fault_3_0.20pu_SCR_4 | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 4 | 10 | Default | 12 | 3p fault | 0 | 20% | 0.45
4063 | TRUE | TRUE | Custom_Fault_3_0.20pu_SCR_5 | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 5 | 10 | Default | 12 | 3p fault | 0 | 20% | 0.45
4064 | TRUE | TRUE | Custom_Fault_3_0.20pu_SCR_6 | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 6 | 10 | Default | 12 | 3p fault | 0 | 20% | 0.45
4065 | TRUE | TRUE | Custom_Fault_2_0.20pu_SCR_2 | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 2 | 10 | Default | 12 | 2p-g fault | 0 | 20% | 0.45
4066 | TRUE | TRUE | Custom_Fault_2_0.20pu_SCR_3 | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 3 | 10 | Default | 12 | 2p-g fault | 0 | 20% | 0.45
4067 | TRUE | TRUE | Custom_Fault_2_0.20pu_SCR_4 | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 4 | 10 | Default | 12 | 2p-g fault | 0 | 20% | 0.45
4068 | TRUE | TRUE | Custom_Fault_2_0.20pu_SCR_5 | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 5 | 10 | Default | 12 | 2p-g fault | 0 | 20% | 0.45
4069 | TRUE | TRUE | Custom_Fault_2_0.20pu_SCR_6 | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 6 | 10 | Default | 12 | 2p-g fault | 0 | 20% | 0.45
4070 | TRUE | TRUE | Custom_Fault_3_0.70pu_SCR_2 | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 2 | 10 | Default | 12 | 3p fault | 0 | 70% | 1.35
4071 | TRUE | TRUE | Custom_Fault_3_0.70pu_SCR_3 | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 3 | 10 | Default | 12 | 3p fault | 0 | 70% | 1.35
4072 | TRUE | TRUE | Custom_Fault_3_0.70pu_SCR_4 | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 4 | 10 | Default | 12 | 3p fault | 0 | 70% | 1.35
4073 | TRUE | TRUE | Custom_Fault_3_0.70pu_SCR_5 | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 5 | 10 | Default | 12 | 3p fault | 0 | 70% | 1.35
4074 | TRUE | TRUE | Custom_Fault_3_0.70pu_SCR_6 | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 6 | 10 | Default | 12 | 3p fault | 0 | 70% | 1.35
4075 | TRUE | TRUE | Custom_Fault_2_0.70pu_SCR_2 | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 2 | 10 | Default | 12 | 2p-g fault | 0 | 70% | 1.35
4076 | TRUE | TRUE | Custom_Fault_2_0.70pu_SCR_3 | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 3 | 10 | Default | 12 | 2p-g fault | 0 | 70% | 1.35
4077 | TRUE | TRUE | Custom_Fault_2_0.70pu_SCR_4 | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 4 | 10 | Default | 12 | 2p-g fault | 0 | 70% | 1.35
4078 | TRUE | TRUE | Custom_Fault_2_0.70pu_SCR_5 | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 5 | 10 | Default | 12 | 2p-g fault | 0 | 70% | 1.35
4079 | TRUE | TRUE | Custom_Fault_2_0.70pu_SCR_6 | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 6 | 10 | Default | 12 | 2p-g fault | 0 | 70% | 1.35
4080 | TRUE | TRUE | Custom_Fault_3_0.20pu_Duration_80 | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 3p fault | 0 | 20% | 0.08
4081 | TRUE | TRUE | Custom_Fault_3_0.20pu_Duration_60 | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 3p fault | 0 | 20% | 0.06
4082 | TRUE | TRUE | Custom_Fault_3_0.20pu_Duration_40 | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 3p fault | 0 | 20% | 0.04
4083 | TRUE | TRUE | Custom_Shift_10_Fault_3_0.20pu | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 3p fault | 0.01 | 20% | 0.04
4084 | TRUE | TRUE | Custom_Shift_20_Fault_3_0.20pu | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 3p fault | 0.02 | 20% | 0.04
4085 | TRUE | TRUE | Custom_Shift_30_Fault_3_0.20pu | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 3p fault | 0.03 | 20% | 0.04
4086 | TRUE | TRUE | Custom_Shift_40_Fault_3_0.20pu | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 3p fault | 0.04 | 20% | 0.04
4087 | TRUE | TRUE | Custom_Shift_50_Fault_3_0.20pu | 1.0651 | 1 | Default | LFSM | Default | 0 | Default | 10 | 10 | Default | 12 | 3p fault | 0.05 | 20% | 0.04

## Event types
Name | Description | X1 description | X1 unit | X2 description | X2 unit
Pref | Pref change | setpoint, base Pn | pu | gradient | 1/s
Pref_unitA | Pref change (unit A, Co-Located) | setpoint (base PnG3 or PnD3) | (pu) | gradient | 1/s
Pref_unitB | Pref change (unit B, Co-Located) | setpoint (base PnG3 or PnD3) | (pu) | gradient | 1/s
Pref_unitC | Pref change (unit C, Co-Located) | setpoint (base PnG3 or PnD3) | (pu) | gradient | 1/s
Pref_unitD | Pref change (unit D, Co-Located) | setpoint (base PnG3 or PnD3) | (pu) | gradient | 1/s
Pavail | Maximum power available change | maximum limit, base Pn | pu | gradient | 1/s
Pavail_unitA | Maximum power available change (unit A, Co-Located) | maximum limit (base PnG3 or PnD3) | (pu) | gradient | 1/s
Pavail_unitB | Maximum power available change (unit B, Co-Located) | maximum limit (base PnG3 or PnD3) | (pu) | gradient | 1/s
Pavail_unitC | Maximum power available change (unit C, Co-Located) | maximum limit (base PnG3 or PnD3) | (pu) | gradient | 1/s
Pavail_unitD | Maximum power available change (unit D, Co-Located) | maximum limit (base PnG3 or PnD3) | (pu) | gradient | 1/s
Qref | Qref change | setpoint, base Pn | pu | gradient | 1/s
Qudroop | Q(U) droop change | Q-U droop | % | - | -
Voltage | Grid voltage change (thevenin) | setpoint, base Un | pu | gradient | 1/s
dVoltage | Delta grid voltage change (thevenin) | setpoint, base Un | pu | gradient | 1/s
Phase | Grid phase change (thevenin) | setpoint | degree | gradient | degree/s
Frequency | Grid frequency change | setpoint | Hz | gradient | Hz/s
SCR | Grid impedance change | SCR | - | X/R | -
3p fault | Three phase fault | residual voltage (across fault reactance), base Un | pu | fault time | s
2p-g fault | Two phase to ground fault | residual voltage (across fault reactance), base Un | pu | fault time | s
2p fault | Two phase fault | residual voltage (across fault reactance), base Un | pu | fault time | s
1p fault | One phase fault | residual voltage (across fault reactance), base Un | pu | fault time | s
3p fault (ohm) | Three phase fault | fault resistance | ohm | fault reactance | ohm
2p-g fault (ohm) | Two phase to ground fault | fault resistance | ohm | fault reactance | ohm
2p fault (ohm) | Two phase fault | fault resistance | ohm | fault reactance | ohm
1p fault (ohm) | One phase fault | fault resistance | ohm | fault reactance | ohm
Clear fault | Clear any fault | N/A | N/A | N/A | N/A
Pref recording | Use external measurement file for Pref signal. First value hold until flattime or initialtime has elapsed. | Relative path to measurementfile | N/A | Scaling factor | -
Qref recording | Use external measurement file for Qref signal. First value hold until flattime or initialtime has elapsed. | Relative path to measurementfile | N/A | Scaling factor | -
Voltage recording | Use external measurement file for the thevenin voltage signal (RMS). First value hold until flattime or initialtime has elapsed. | Relative path to measurementfile | N/A | Scaling factor | -
Inst. Voltage recording | Only supported for PSCAD. Use external measurement file for the thevenin instantaneous voltages. Time value ignored. | Relative path to measurementfile | N/A | Scaling factor | -
Phase recording | Use external measurement file for the thevenin voltage phase signal. First value hold until flattime or initialtime has elapsed. | Relative path to measurementfile | N/A | Scaling factor | -
Frequency recording | Use external measurement file for the thevenin voltage frequency signal. First value hold until flattime or initialtime has elapsed. | Relative path to measurementfile | N/A | Scaling factor | -
Signal 1 | Custom signal 1 change (Use t < 0s to initialize) | value | ? | gradient | ?/s
Signal 2 | Custom signal 2 change (Use t < 0s to initialize) | value | ? | gradient | ?/s
Signal 3 | Custom signal 3 change (Use t < 0s to initialize) | value | ? | gradient | ?/s
Signal 4 | Custom signal 4 change (Use t < 0s to initialize) | value | ? | gradient | ?/s
Signal 5 | Custom signal 5 change (Use t < 0s to initialize) | value | ? | gradient | ?/s
Signal 6 | Custom signal 6 change (Use t < 0s to initialize) | value | ? | gradient | ?/s
Signal 7 | Custom signal 7 change (Use t < 0s to initialize) | value | ? | gradient | ?/s
Signal 8 | Custom signal 8 change (Use t < 0s to initialize) | value | ? | gradient | ?/s
Signal 9 | Custom signal 9 change (Use t < 0s to initialize) | value | ? | gradient | ?/s
Signal 10 | Custom signal 10 change (Use t < 0s to initialize) | value | ? | gradient | ?/s
Signal 1 recording | Use external measurement file for custom signal 1. First value hold until flattime or initialtime has elapsed. | Relative path to measurementfile | N/A | Scaling factor | -
Signal 2 recording | Use external measurement file for custom signal 2. First value hold until flattime or initialtime has elapsed. | Relative path to measurementfile | N/A | Scaling factor | -
Signal 3 recording | Use external measurement file for custom signal 3. First value hold until flattime or initialtime has elapsed. | Relative path to measurementfile | N/A | Scaling factor | -
Signal 4 recording | Use external measurement file for custom signal 4. First value hold until flattime or initialtime has elapsed. | Relative path to measurementfile | N/A | Scaling factor | -
Signal 5 recording | Use external measurement file for custom signal 5. First value hold until flattime or initialtime has elapsed. | Relative path to measurementfile | N/A | Scaling factor | -
Signal 6 recording | Use external measurement file for custom signal 6. First value hold until flattime or initialtime has elapsed. | Relative path to measurementfile | N/A | Scaling factor | -
Signal 7 recording | Use external measurement file for custom signal 7. First value hold until flattime or initialtime has elapsed. | Relative path to measurementfile | N/A | Scaling factor | -
Signal 8 recording | Use external measurement file for custom signal 8. First value hold until flattime or initialtime has elapsed. | Relative path to measurementfile | N/A | Scaling factor | -
Signal 9 recording | Use external measurement file for custom signal 9. First value hold until flattime or initialtime has elapsed. | Relative path to measurementfile | N/A | Scaling factor | -
Signal 10 recording | Use external measurement file for custom signal 10. First value hold until flattime or initialtime has elapsed. | Relative path to measurementfile | N/A | Scaling factor | -
PF disconnect all ref. | In Powerfactory out-of-service all references (including custom signals) to plant. For initialization testing purposes. | N/A | N/A | N/A | N/A
PF force asymmetrical | Force case to be simulated asymmetricaly. | N/A | N/A | N/A | N/A

## RfG cases overview
Rank | Name | Category | Comment
1 | RfG_SS_flatrun_Q1 | Steady state - model performance/convergence | PRE-run cases to check model is correctly setup with MTB and can properly flatrun.
2 | RfG_SS_flatrun_Q2 |  | Test of model performance, flatrun in several operation points and Q-modes
3 | RfG_SS_flatrun_Q3 |  | -
4 | RfG_SS_flatrun_Q4 |  | -
5 | RfG_SS_flatrun_Q5 |  | -
6 | RfG_SS_flatrun_Q6 |  | -
7 | RfG_SS_flatrun_Uctrl_min |  | -
8 | RfG_SS_flatrun_Uctrl_max |  | -
9 | RfG_SS_flatrun_PFctrl1 |  | -
10 | RfG_SS_flatrun_PFctrl2 |  | -
11 | RfG_P_step_up_0.0_0.5 | Active power | Test of active power ramping. Check compliance with max ramp rate 20%Pn/min
12 | RfG_P_step_up_0.5_0.7 |  | Test model function in various operation points.
13 | RfG_P_step_up_0.7_1.0 |  | -
14 | RfG_P_step_down_1.0_0.7 |  | -
15 | RfG_P_step_down_0.7_0.5 |  | -
16 | RfG_P_step_down_0.5_0.0 |  | -
17 | RfG_FSM_step1 | Frequency | Test of FSM (full frequency range)
18 | RfG_FSM_step2 |  | Test FSM follows droop correctly, case should ensure half power change of FSM limit (+/-5% power) (not working yet)
19 | RfG_LFSM-OU_step1 |  | Test of LFSM (full range)
20 | RfG_LFSM-O_ramp |  | Test of LFSM-O with ramp
21 | RfG_LFSM-U_ramp |  | Test of LFSM-U with ramp
22 | RfG_FSM_LFSM-O_ramp |  | Test of transition between FSM and LFSM during ramping.
23 | RfG_FSM_LFSM-U_ramp |  | -
24 | RfG_FSM_LFSM-O_step |  | Test of transition between FSM and LFSM during steps
25 | RfG_FSM_LFSM-U_step |  | -
26 | RfG_LFSM-O_Pavail |  | Test of LFSM-O with limited available power. PPC setpoint does not match the actual power production, so can it handle this ?
27 | RfG_LFSM-U_Pavail |  | Test of LFSM-U with limited available power. PPC setpoint does not match the actual power production, so can it handle this ?
28 | RfG_U-Q/Pn_Neutral | Reactive power capability + voltage control | Test of reactive power capability. (fixed Q setpoint and varying voltage), Q = 0
29 | RfG_U-Q/Pn_Neutral_stab |  | Test of stability when fixed Q setpoint and varying voltage, Q = 0. OBS!! This case should not result in more than 10% voltage drop at POC. The case is setup such that voltages are changes directly on the grid source behind impedance. Therefore based on the grid impedance and powerflow, potentially the voltage drop in POC can be larger than 10%. If that is the case the setup should be changed. Adjust the voltage change at source to realise the correct voltage changes at POC. both the up and down step.
30 | RfG_U-Q/Pn_underEX |  | Test of reactive power capability. (fixed Q setpoint and varying voltage), Q = -0.33pu
31 | RfG_U-Q/Pn_overEX |  | Test of reactive power capability. (fixed Q setpoint and varying voltage), Q = 0.33pu
32 | RfG_PQ/Pn_Neutral1 |  | Test of reactive power capability when changing P setpoint, Q = 0. Important: For large plants and low SCR it may not be realistic to change power from 1pu-0 without changing the POC voltage too much. When relevant split the simulation into multiple with different starting points.
33 | RfG_PQ/Pn_Neutral2 |  | Test of reactive power capability when changing P setpoint, Q = 0
34 | RfG_PQ/Pn_underEX1 |  | Test of reactive power capability when changing P setpoint, Q = -0.33pu
35 | RfG_PQ/Pn_underEX2 |  | Test of reactive power capability when changing P setpoint, Q = -0.33pu
36 | RfG_PQ/Pn_overEX1 |  | Test of reactive power capability when changing P setpoint, Q = 0.33pu
37 | RfG_PQ/Pn_overEX2 |  | Test of reactive power capability when changing P setpoint, Q = 0.33pu
38 | RfG_Ucontrol_Scmin |  | Test of reactive power capability and voltage control performance (minimum SC). Plant should comply with rise time 1s and settling time 5s and also overshoot should be less than 20% of the step change in reactive power. This for each voltage step in the simulation. Both away from and back to normal operation voltage.
39 | RfG_Ucontrol_Sctune |  | Test of reactive power capability and voltage control performance ("medium" SC)
40 | RfG_Ucontrol_Scmax |  | Test of reactive power capability and voltage control performance (max SC)
41 | RfG_Ucontrol_FRTsensitivity |  | Test how voltage control performs just around FRT threshold. (Focus is plant performance, plant should not suddenly reduce the reactive current when going from "low" voltage and into FRT). Important: This simulation is not realistic scenario and should not be used for GC compliance, but is a screening of stability risk/voltage control performance. It is not a requirement that plants can handle 3 consecutive voltage drops in this manner. When relevant simulation should be split into multiple cases and modified in order to make scenarious representative of real operation and do further assessment of any stability risk
42 | RfG_Ucontrol_FRTsensitivity-ramp |  | Test how voltage control performs just around FRT threshold. (Focus is plant performance, plant should not suddenly reduce the reactive current when going from "low" voltage and into FRT). Now with ramping voltage transition from above to below FRT limit
43 | RfG_Uarea_Qreq_1(up) | Reactive power in full voltage range | Test plant can operate in full voltage range and what will do when voltage goes below U-Q/Pn limits (fixed Q setpoint)
44 | RfG_Uarea_Qreq_2(up) |  | -
45 | RfG_Uarea_Qreq_1(down) |  | Test plant can operate in full voltage range and what will do when voltage goes below U-Q/Pn limits (fixed Q setpoint)
46 | RfG_Uarea_Qreq_2(down) |  | Note: Depending on system, steps 2 and 3 may be the same as step 1. Step 1 goes to limits of UQ, step 2 goes to continues voltage limit, step 3 goes to time restricted voltage limit (FRT limit)
47 | RfG_Uarea_Qreq_3(down) |  | -
48 | RfG_Uarea_Q(U)req_1(up) |  | Test plant can operate in full voltage range and what will do when voltage goes below U-Q/Pn limits (U-control)
49 | RfG_Uarea_Q(U)req_2(up) |  | -
50 | RfG_Uarea_Q(U)req_1(down) |  | Test plant can operate in full voltage range and what will do when voltage goes below U-Q/Pn limits (U-control). In voltage control, plant must be able to keep delivering atleast the minimum required Q of 33%
51 | RfG_Uarea_Q(U)req_2(down) |  | Note: Depending on system, steps 2 and 3 may be the same as step 1. Step 1 goes to limits of UQ, step 2 goes to continues voltage limit, step 3 goes to time restricted voltage limit (FRT limit)
52 | RfG_Uarea_Q(U)req_3(down) |  | -
53 | RfG_Q_control_up | Q-mode and Pf-mode regulation | Test performance in Q-control, when changing setpoint. Important: Plant should be allowed time to optimize tap changers between each Q step and depending on SCR, Q steps should not be so large the POC voltage is changed drastically. When relevant extend the time period of each step or split the simulation into multiple with different starting points.
54 | RfG_Q_control_down |  | Test performance in Q-control, when changing setpoint. Important: same as above
55 | RfG_Qpf_PFref-change |  | Test performance in Pf-control, when changing power factor setpoint. Important: same as above
56 | RfG_Qpf_Pref-change |  | Test performance in Pf-control, when changing P setpoint. Important: same as above
57 | RfG_SystemProtect_Q | Systemguard | Test model includes SIPS function and performance is compliant in Q-control. Response time must be less than 1s and fully activated within 10sec.
58 | RfG_SystemProtect_QU |  | Test model includes SIPS function and performance is compliant in U-control. Response time must be less than 1s and fully activated within 10sec.
59 | RfG_SystemProtect+fault |  | Test of SIPS functionality following fault. The main purpose is to check response time of the SIPS when activated just after a fault is cleared. SIPS requirement says response time must be less than 1s and fully activated within 10sec. However, in case of SIPS activation after fault this can be challenge since PPC freeze during fault. The SIPS should still activate as fast as possible after fault, though we accept PFAPR has priority but SIPS time should not be unnecessarily long. In general the 10s settling time of SIPS target is more critical than the 1s response time and in general it is expected plant still comply with the settling time of 10s but response time is more than 1s. If response time is more than 5s, developer have to argue why that is reasonable. So if power is restored to nominal for several seconds before reacting to the SIPS activation this must be explained.
60 | RfG_MaxPhaseJump1 | Plant robustness | Test plant is compliant with 20deg phase jumps (large jumps)
61 | RfG_MaxPhaseJump2 |  | Test of phasejump robustness with several consecutive smaller phasejumps adding up to 20deg over 3 periods
62 | RfG_MaxRoCoF1 |  | Test of robusstness for RoCoF (RoCoF of either 2Hz/s or 0.5Hz/s for long time)
63 | RfG_MaxRoCoF2 |  | Test of robusstness for RoCoF (RoCoF of either 4Hz/s for just 100ms or 20Hz/s for 20ms.)
64 | RfG_MaxRoCoF_CurveOF |  | Test of Rocof robustness (more realistic frequency event curve with varying RoCof - over frequency
65 | RfG_MaxRoCoF_CurveUF |  | Test of Rocof robustness (more realistic frequency event curve with varying RoCof - under frequency
66 | RfG_LVFRT_profile |  | Test of LVRT robustness (standard profile)
67 | RfG_LVFRT_profile_Pref_05 |  | Test of LVRT robustness (standard profile) with 0.5 p.u. active power.
68 | RfG_LVFRT_profil_Pref_05_Pavail |  | Test of LVRT robustness (standard profile) with 0.5 p.u. active power and 0.5 p.u. available power.
69 | RfG_OVRT_profile |  | Test of HVRT robustness (standard profile)
70 | RfG_Fault_3_0 | Faults | Fault simulations test of robustness/stability and compliance with PFAPR + reactive fault current
71 | RfG_Fault_3_20 |  | -
72 | RfG_Fault_3_40 |  | -
73 | RfG_Fault_3_60 |  | -
74 | RfG_Fault_3_80 |  | -
75 | RfG_Fault_3_thres |  | Screening what happens just around FRT threshold - any toggling ?
76 | RfG_Fault_2_0 |  | -
77 | RfG_Fault_2_20 |  | -
78 | RfG_Fault_2_40 |  | -
79 | RfG_Fault_2_60 |  | -
80 | RfG_Fault_2_80 |  | -
81 | RfG_Fault_2_thres |  | Screening what happens just around FRT threshold - any toggling ?
82 | RfG_Fault_1_0 |  | -
83 | RfG_Fault_1_20 |  | -
84 | RfG_Fault_1_40 |  | -
85 | RfG_Fault_1_60 |  | -
86 | RfG_Fault_1_80 |  | -
87 | RfG_Fault_1_thres |  | Screening what happens just around FRT threshold - any toggling ?
88 | RfG_Voltage-support |  | Test of reactive fault current contribution, match required static
89 | RfG_Fault_1_restrike |  | Test of robustness for consecutive faults - single fase with auto reclosure. 2 different faults each with double strike.
90 | RfG_Fault_3_double |  | Test of robustness for consecutive faults - 3 phase fault, 2 individual faults in a row
91 | RfG_Fault_2_double |  | Test of robustness for consecutive faults - 2 phase fault, 2 individual faults in a row
92 | RfG_Fault_3_SCR |  | Test of stability, 3 fase fault with impedance change at fault clearing. (jump from SC "tune" to SC min)
93 | RfG_Fault_2_SCR |  | Test of stability, 2 fase fault with impedance change at fault clearing. (jump from SC "tune" to SC min)
94 | RfG_LFSM-OU_step2 | Extra Frequency tests | Test of LFSM follows correct droop. Designed to ensure first steps result in +/- 25% power change, then +/- 50% power change
95 | RfG_LFSM-OU_step1+FSM |  | The original (ION) step test of LFSM, now with FSM active
96 | RfG_FSM_rec_pstep |  | Test with playback of real frequency measurement. Test of FSM based on f-measurement while changing active power setpoint. Constant and minor variations in frequency barely activating FSM while changing active power reference. Mainly test that model performance/convergence can handle real signal with constant variation. Potentially also indicator of real plant challenges.
97 | RfG_LFSMO_ramp+pstep |  | Test of LFSM-O activation during setpoint change (when active power varies). When exit LFSM plant should return to same Power as was at LFSM activation and then continue ramp from there.
98 | RfG_LFSM-O_Q_control | Extra testing reactive power/voltage control | Test of LFSM-O activation during Q setpoint change. (mostly about model robustness/performance; can model regulate active and reactive power at the same time. Not so much compliance)
99 | RfG_Ucontrol_LFSM-O |  | Test of simultanious voltage control and frequency control. (mostly about model robustness/performance; can model regulate active and reactive power at the same time. Not so much compliance)
100 | RfG_Ucontrol_Phasejump |  | Test of Ucontrol, voltage change and phasejump. (Plant performance / compliance)
101 | RfG_Ucontrol_SCR |  | Test of Ucontrol, voltage change and impedans change. (Plant performance / compliance)
102 | RfG_Ucontrol_Fault |  | Test of Ucontrol, voltage change and fault. (Plant performance / compliance)
103 | RfG_Ucontrol_Fault_FRTlimit |  | Test of Ucontrol, fault event where voltage covers to just above FRT limit. Test to see plant correctly starts voltage control and is not stuck in FRT mode. (Plant performance / compliance)
104 | RfG_Ucontrol_Scmin_Droop_2 |  | Test of Ucontrol with a droop of 2%. Ensures droop-range described in RfG.
105 | RfG_Ucontrol_Scmin_Droop_4 |  | Test of Ucontrol with a droop of 4%. Ensures droop-range described in RfG.
106 | RfG_Ucontrol_Scmin_Droop_7 |  | Test of Ucontrol with a droop of 7%. Ensures droop-range described in RfG.
107 | RfG_Ucontrol_rec |  | Test with playback of real voltage measurement. Ucontrol can, from the RfG, have a deadband from zero to +/- 5% of reference 1 pu network voltage. Mainly tests of Ucontrol deadband and model performance/convergence can handle real signal with constant variation.
108 | RfG_Pavail_variation | Extra robustness | Test model functions when varying available active power. (in EMT model look for oscillations as power varies). When available power increases, the normal power gradient must be used.
109 | RfG_Pavail_step_P_step_up_05_10 |  | Test model functions when varying available active power and active power ramping. Check compliance with max ramp rate 20%Pn/min when available increases.
110 | RfG_MaxPhaseJump_Extreme |  | Test of phase jump robustness, going beyond 20deg (just screening of plant capability) 30deg and 40 deg. (also model robustness)
111 | RfG_RoCoF_ACER-CurveOF |  | Test of RoCoF robustness, the curve from RfG 2.0 (currently more strict than national requirement)
112 | RfG_RoCoF_ACER-CurveUF |  | Test of RoCoF robustness, the curve from RfG 2.0 (currently more strict than national requirement)
113 | RfG_RoCoF+PhaseJump1 |  | Test of robustness, combination of RoCoF and phase jump events
114 | RfG_RoCoF+PhaseJump2 |  | Test of robustness, combination of RoCoF and phase jump events
115 | RfG_Fault_3_0_NotDef | Extra faults | Fault simulations with the "not default" Q-mode. Typically voltage control. test of robustness/stability and compliance with PFAPR + reactive fault current
116 | RfG_Fault_3_20_NotDef |  | -
117 | RfG_Fault_3_40_NotDef |  | -
118 | RfG_Fault_3_60_NotDef |  | -
119 | RfG_Fault_3_80_NotDef |  | -
120 | RfG_Fault_3_thres_NotDef |  | Screening what happens just around FRT threshold - any toggling ?
121 | RfG_Fault_2_20_NotDef |  | -
122 | RfG_Fault_2_40_NotDef |  | -
123 | RfG_Fault_2_60_NotDef |  | -
124 | RfG_Fault_2_80_NotDef |  | -
125 | RfG_Fault_1_20_NotDef |  | -
126 | RfG_Fault_1_40_NotDef |  | -
127 | RfG_Fault_1_60_NotDef |  | -
128 | RfG_Fault_1_80_NotDef |  | -
129 | RfG_Fault_3_SCR_NotDef |  | Test of plant stability, 3 fase fault with impedance change at fault clearing. (jump from SC "tune" to SC min)
130 | RfG_Fault_2_SCR_NotDef |  | Test of plant stability, 2 fase fault with impedance change at fault clearing. (jump from SC "tune" to SC min)
131 | RfG_Fault_3_UnderThres_NotDef |  | Test of respons just below FRT threshold in "not default" Q-mode. 3phase fault
132 | RfG_Fault_3_UnderThres |  | Test of respons just below FRT threshold in default Q-mode. 3phase fault
133 | RfG_Fault_1_UnderThres |  | Test of respons just below FRT threshold in default Q-mode. 1phase fault
134 | RfG_Fault_2_double_NotDef |  | Test of robustness for consecutive faults - 2 phase fault, 2 individual faults in a row. With plant in "not default" Q-mode
135 | RfG_Fault_double-mix_SCR |  | Test of robustness for consecutive faults - mix of unbalanced/balanced event. First 2 phase then 3 phase faults + grid impedance change in the end.
136 | RfG_Fault_3_20_WG |  | Fault simulation, test plant stability in weak grid outside required compliance. Always SCR = 2
137 | RfG_Fault_2_20_WG |  | Fault simulation, test plant stability in weak grid outside required compliance. Always SCR = 2
138 | RfG_Fault_3_RoCoF_curveOF |  | 3phase fault and RoCoF event. Plant stability and model robustness. Further used to evaluate plant can respond to LFSM fast enough after fault. LFSM-O requirement says response time must be as fast as possible and requires explanation if this is more than 2s. However, in case of frequency event after fault this can be challenge since PPC freeze during fault. The LFSM-O should still activate as fast as possible after fault, though we accept PFAPR has priority but LFSM time should not be unnecessarily long. If plants take more than 5 sec /(or when PFAPR has finished, if less than 5s) to start reacting on frequency change, developer have to argue why that is reasonable. So if power is restored to nominal for several seconds before reacting to the LFSM-O this must be explained.
139 | RfG_Fault_3_RoCoF_curveUF |  | 3phase fault and RoCoF event. Plant stability and model robustness
140 | RfG_Fault_3_SCR_freqStep1 |  | 3phase fault, impedance change and frequency steps (frequency back to normal after 6s, more than max PPC freeze time). Plant stability and model robustness. Further used to evaluate plant can respond to LFSM fast enough after fault. LFSM-O requirement says response time must be as fast as possible and requires explanation if this is more than 2s. However, in case of frequency event after fault this can be challenge since PPC freeze during fault. The LFSM-O should still activate as fast as possible after fault, though we accept PFAPR has priority but LFSM time should not be unnecessarily long. If plants take more than 5 sec /(or when PFAPR has finished, if less than 5s) to start reacting on frequency change, developer have to argue why that is reasonable. So if power is restored to nominal for several seconds before reacting to the LFSM-O this must be explained.
141 | RfG_Fault_3_SCR_freqStep2 |  | 3phase fault, impedance change and frequency steps (frequency back to normal after 4s, less than max PPC freeze time). Plant stability and model robustness
142 | RfG_SCR_step_Max-Min |  | Model robustness - grid impedance change from Max to Min SC. In default Q-mode. Unrealistic case, not used for compliance, but can screen for stability challenges
143 | RfG_SCR_step_Max-Min_NotDef |  | Model robustness - grid impedance change from Max to Min SC. In "not default" Q-mode. Unrealistic case, not used for compliance, but can screen for stability challenges
144 | RfG_Fault_rec_1_Q |  | Plant stability during faults with critical voltage recovery. (recording from system model simulation). Q-control
145 | RfG_Fault_rec_1_Q(U) |  | Plant stability during faults with critical voltage recovery. (recording from system model simulation). U-control
146 | RfG_Fault_rec_2_Q |  | Recording of double fault in system model. Plant stability in Q-control
147 | RfG_Fault_rec_2_Q(U) |  | Recording of double fault in system model. Plant stability in U-control
148 | RfG_Fault_rec_3_Q |  | Recording of fault with very slow voltage recovery. Plant stability in Q-control
149 | RfG_Fault_rec_3_Q(U) |  | Recording of fault with very slow voltage recovery. Plant stability in U-control
150 | RfG_TRF_GND_Fault_3_0.20pu_Scmin |  | Fault simulations with the "default" Q-mode and HV transformer grounded. Test of reactive-fault current, robustness and stability.
151 | RfG_TRF_GND_Fault_3_0.20pu_Scmax |  | -
152 | RfG_TRF_GND_Fault_2_0.20pu_Scmin |  | -
153 | RfG_TRF_GND_Fault_2_0.20pu_Scmax |  | -
154 | RfG_TRF_GND_Fault_2g_0.20pu_Scmin |  | -
155 | RfG_TRF_GND_Fault_2g_0.20pu_Scmax |  | -
156 | RfG_TRF_GND_Fault_1_0.20pu_Scmin |  | -
157 | RfG_TRF_GND_Fault_1_0.20pu_Scmax |  | -
158 | RfG_Shift_05_Fault_3_0.20pu |  | Short (60ms) fault simulations with the "default" Q-mode. The fault is delayed with 5ms to validate plant stability and robustness, when the simulated fault time is not a product of 100ms or equal to assumed PPC sampling time.
159 | RfG_Shift_55_Fault_3_0.40pu |  | Short (60ms) fault simulations with the "default" Q-mode. The fault is delayed with 55ms to validate plant stability and robustness, when the simulated fault time is not a product of 100ms or equal to assumed PPC sampling time.
160 | RfG_Pavail_Fault_3_0.20pu |  | Fault simulations with the "default" Q-mode and with 0.5 p.u. active power and 0.5 p.u. available power. Test of reactive-fault current, PFAPR, robustness and stability.
161 | RfG_Pavail_Fault_2_0.20pu |  | -
162 | RfG_proc_VoltageRise_1.2 | Test of protection functionality in model | Testing different overvoltage levels, when will plant trip.
163 | RfG_proc_VoltageRise_1.3 |  | Important: All simulations in this section is not realistic and so should not be used for plant compliance. However, the protection functionality in the model must be proven, and these simulations is a proposal for that
164 | RfG_proc_VoltageRise_1.4 |  | -
165 | RfG_proc_VoltageRise_1.5 |  | -
166 | RfG_proc_VoltageRise_insta_min |  | test with transient overvoltage spikes with increasing magnitude. (does model contain any instantinous protection? Mainly EMT model). Testing with minimum SC
167 | RfG_proc_VoltageRise_insta_max |  | test with transient overvoltage spikes with increasing magnitude. (does model contain any instantinous protection? Mainly EMT model). Testing with maximum SC
168 | RfG_proc_Fault_3_0.8pu |  | Test with fault lasting 60seconds, when will plant trip
169 | RfG_proc_Fault_3_0.6pu |  | -
170 | RfG_proc_Fault_3_0.40pu |  | -
171 | RfG_proc_Fault_3_0.20pu |  | -
172 | RfG_proc_Freq_51.6Hz |  | Test with frequency just above limit, will plant trip ?
173 | RfG_proc_Freq_47.4Hz |  | Test with frequency just below limit, will plant trip ?
174 | RfG_proc_Freq_limit_up |  | Test with frequency increasing in steps, when will plant trip ? (does model seem to include all protection functions)
175 | RfG_proc_Freq_limit_down |  | Test with frequency decreasing in steps, when will plant trip ? (does model seem to include all protection functions)
176 | RfG_proc_Fault_1_0.05pu | Max 1fase fault current | Test if plant can handle the maximum 1fase fault current. (simulation must be made with HV trafo grounded)

## DCC cases overview
Rank | Name | Category | Comment
1001 | PRE_SS_flatrun_Q1 | Steady State - model performance/convergence | PRE-run cases to check model is correctly setup with MTB and can properly flatrun.
1002 | PRE_SS_flatrun_Q2 |  | Test of model performance
1003 | PRE_SS_flatrun_Q3 |  | -
1004 | PRE_SS_flatrun_Q4 |  | -
1005 | PRE_SS_flatrun_Q5 |  | -
1006 | DCC_Fault_3_0 | Fault | Fault simulations test of robustness/stability and compliance with PFAPR
1007 | DCC_Fault_3_20 |  | -
1008 | DCC_Fault_3_40 |  | -
1009 | DCC_Fault_3_80 |  | -
1010 | DCC_Fault_2_0 |  | -
1011 | DCC_Fault_2_20 |  | -
1012 | DCC_Fault_2_40 |  | -
1013 | DCC_Fault_2_80 |  | -
1014 | DCC_Fault_1_0 |  | -
1015 | DCC_Fault_1_20 |  | -
1016 | DCC_Fault_1_40 |  | -
1017 | DCC_Fault_1_80 |  | -
1018 | DCC_Fault_1_restrike |  | Test of robustness for consecutive faults - single fase with auto reclosure. 2 different faults each with double strike.
1019 | DCC_Fault_3_double |  | Test of robustness for consecutive faults - 3 phase fault, 2 individual faults in a row
1020 | DCC_Fault_2_double |  | Test of robustness for consecutive faults - 2 phase fault, 2 individual faults in a row
1021 | DCC_Fault_3_20_short |  | -
1022 | DCC_Fault_2_20_short |  | -
1023 | DCC_Fault_3_20_WG |  | Test of stability, SCR of 3
1024 | DCC_Fault_2_20_WG |  | Test of stability, SCR of 3
1025 | DCC_Fault_3_SCR |  | Test of stability, 3 fase fault with impedance change at fault clearing. (jump from SC "tune" to SC min)
1026 | DCC_Fault_2_SCR |  | Test of stability, 2 fase fault with impedance change at fault clearing. (jump from SC "tune" to SC min)
1027 | DCC_Fault_3_SCR_freqStep |  | Test of stability, 3 fase fault with impedance change at fault clearing. (jump from SC "tune" to SC min) with frequency event post-fault
1028 | DCC_FRTsensitivity |  | Screening what happens just around FRT threshold - any toggling ? (Step)
1029 | DCC_FRTsensitivity-ramp |  | Screening what happens just around FRT threshold - any toggling ? (Ramp)
1030 | DCC_SCR_step_Max-Min |  | Test of robustness for SCR change (max - min - max)
1031 | DCC_LVFRT(kat7)_Profile |  | Test of robustnes towards LVFRT (relevant for category 7 demand facilities)
1032 | DCC_OVFRT(SP)_Profile |  | Test of robustnes towards OVFRT (relevant for co-located demand facilities)
1033 | DCC_Fault_rec_1 |  | Facility stability during faults with critical voltage recovery. (recording from system model simulation).
1034 | DCC_Fault_rec_3 |  | Recording of fault with very slow voltage recovery. (recording from system model simulation).
1035 | DCC_TRF_GND_Fault_3_0.20pu_Scmin |  | Fault simulations with the HV transformer grounded. Test of robustness and stability.
1036 | DCC_TRF_GND_Fault_3_0.20pu_Scmax |  | -
1037 | DCC_TRF_GND_Fault_2_0.20pu_Scmin |  | -
1038 | DCC_TRF_GND_Fault_2_0.20pu_Scmax |  | -
1039 | DCC_TRF_GND_Fault_2g_0.20pu_Scmin |  | -
1040 | DCC_TRF_GND_Fault_2g_0.20pu_Scmax |  | -
1041 | DCC_TRF_GND_Fault_1_0.20pu_Scmin |  | -
1042 | DCC_TRF_GND_Fault_1_0.20pu_Scmax |  | -
1043 | DCC_SystemGuard | Systemguard | Test model includes SIPS function. Response time must be less than 1s and fully activated within 10sec.
1044 | DCC_SystemGuard+fault |  | Test of SIPS functionality following fault. The main purpose is to check response time of the SIPS when activated just after a fault is cleared. SIPS requirement says response time must be less than 1s and fully activated within 10sec.
1045 | DCC_MaxPhaseJump | Facility Robustness | Test plant is compliant with 20deg phase jumps (large jumps)
1046 | DCC_MaxPhaseJump2 |  | Test of phasejump robustness with several consecutive smaller phasejumps adding up to 20deg over 3 periods
1047 | DCC_MaxRoCoF1 |  | Test of robusstness for RoCoF (RoCoF of either 2Hz/s or 0.5Hz/s for long time)
1048 | DCC_MaxRoCoF2 |  | Test of robusstness for RoCoF (RoCoF of either 4Hz/s for just 100ms or 20Hz/s for 20ms.)
1049 | DCC_MaxRoCoF_CurveOF |  | Test of Rocof robustness (more realistic frequency event curve with varying RoCof - over frequency
1050 | DCC_MaxRoCoF_CurveUF |  | Test of Rocof robustness (more realistic frequency event curve with varying RoCof - under frequency
1051 | DCC_MaxPhaseJump_Extreme_min |  | Test of phase jump robustness, going beyond 20deg (just screening of plant capability) 30deg and 40 deg. (also model robustness)
1052 | DCC_MaxPhaseJump_Extreme_max |  | -
1053 | DCC_RoCoF+PhaseJump1 |  | Test of facility robustness to combinded RoCoF and phase jump respond.
1054 | DCC_RoCoF+PhaseJump2 |  | -
1055 | DCC_LFSM-OU_step1 | Frequency | Test of facility robustness to combined over- and under-frequency. Validation of facility LFSM-U functionality (category 7 facility).
1056 | DCC_LFSM-O_ramp |  | Test of facility robustness to over-frequency.
1057 | DCC_LFSM-U_ramp |  | Test of facility robustness to under-frequency. Validation of facility LFSM-U functionality (category 7 facility).
1058 | DCC_LFDD |  | Validation of LFDD functionality with 1.0 p.u. active power
1059 | DCC_LFDD_P05 |  | Validation of LFDD functionality with 0.5 p.u. active power
1060 | DCC_LFDD+Fault |  | Validation of LFDD functionality post-fault. Relevant for all facilities that remains connected to the grid.
1061 | DCC_Faera-O |  | Test of facility robustness and protection to over-frequency beyond 51.5 Hz
1062 | DCC_Faera-U |  | Test of facility robustness and protection to under-frequency beyond 47-5 Hz
1063 | DCC_Uarea_Qreq_1(up) | Reactive Power Regulation and Voltage Stability (Normal Operation Area) | Test of reactive power requirement during voltage changes (within the normal operation area)
1064 | DCC_Uarea_Qreq_2(up) |  | -
1065 | DCC_Uarea_Qreq_1(down) |  | -
1066 | DCC_Uarea_Qreq_2(down) |  | -
1067 | DCC_Uarea_Qreq_3(down) |  | -
1068 | DCC_Uarea_ramp_up |  | -
1069 | DCC_Uarea_ramp_down |  | -
1070 | DCC_Overvoltage_characteristic | Extra Voltage Stability | Testing different overvoltage levels, when will plant trip
1071 | DCC_Undervoltage_characteristic |  | Testing different undervoltage levels, when will plant trip
1072 | DCC_VoltageRise_insta_min |  | test with transient overvoltage spikes with increasing magnitude. (does model contain any instantinous protection? Mainly EMT model). Testing with minimum SC
1073 | DCC_VoltageRise_insta_max |  | test with transient overvoltage spikes with increasing magnitude. (does model contain any instantinous protection? Mainly EMT model). Testing with maximum SC
1074 | DCC_VoltageDip_insta_min |  | test with transient undervoltage spikes with increasing magnitude. (does model contain any instantinous protection? Mainly EMT model). Testing with minimum SC
1075 | DCC_VoltageDip_insta_max |  | test with transient undervoltage spikes with increasing magnitude. (does model contain any instantinous protection? Mainly EMT model). Testing with maximum SC
1076 | DCC_freqRise_insta_Source |  | test with transient overfrequency spikes with increasing magnitude. (does model contain any instantinous protection? Mainly EMT model).
1077 | DCC_freqDip_insta_Source |  | test with transient underfrequency spikes with increasing magnitude. (does model contain any instantinous protection? Mainly EMT model).
1078 | DCC_proc_VoltageRise_1.2 |  | Test of different overvoltage levels. When will the facility trip?
1079 | DCC_proc_VoltageRise_1.3 |  | -
1080 | DCC_proc_VoltageRise_1.4 |  | -
1081 | DCC_proc_VoltageRise_1.5 |  | -
1082 | DCC_proc_Fault_3_0.8pu | Test of protection functionality in model | Test of different lowvoltage levels. When will the facility trip?
1083 | DCC_proc_Fault_3_0.6pu |  | -
1084 | DCC_proc_Fault_3_0.40pu |  | -
1085 | DCC_proc_Fault_3_0.20pu |  | -
1086 | DCC_proc_Fault_1_0.05pu |  | -

## Unit cases overview
Rank | Name | Category | Comment
2001 | UNT_SS_flatrun_Q1 | Steady state - model performance/convergence | Test of model performance, flatrun in several operation points and Q-modes
2002 | UNT_SS_flatrun_Q2 |  | -
2003 | UNT_SS_flatrun_Q3 |  | -
2004 | UNT_SS_flatrun_Q4 |  | -
2005 | UNT_SS_flatrun_Q5 |  | -
2006 | UNT_SS_flatrun_Q6 |  | -
2007 | UNT_P_step_up_0.5_0.7 | Active power regulation | Model performance during active power setpoint change
2008 | UNT_Q_control_up | Reactive power regulation | Model performance during Q setpoint change
2009 | UNT_U-Q/Pn_Neutral |  | Model performance during voltage variations
2010 | Unit_Uarea_Qreq_1(up) |  | Test of reactive power requirement during voltage changes (within the normal operation area)
2011 | Unit_Uarea_Qreq_2(up) |  | -
2012 | Unit_Uarea_Qreq_1(down) |  | -
2013 | Unit_Uarea_Qreq_2(down) |  | -
2014 | Unit_Uarea_Qreq_3(down) |  | -
2015 | UNT_Uarea_ramp_up |  | -
2016 | UNT_Uarea_ramp_down |  | -
2017 | UNT_fArea | Robustness test / model performance | Test model performance in full frequency area
2018 | UNT_LVFRT_profile |  | Test model performance in LVRT
2019 | UNT_OVRT_profile |  | Test model performance in HVRT
2020 | UNT_Fault_3_0 | Faults | Fault simulations test of robustness/stability
2021 | UNT_Fault_3_20 |  | -
2022 | UNT_Fault_3_40 |  | -
2023 | UNT_Fault_3_80 |  | -
2024 | UNT_Fault_2_0 |  | -
2025 | UNT_Fault_2_20 |  | -
2026 | UNT_Fault_2_40 |  | -
2027 | UNT_Fault_2_80 |  | -
2028 | UNT_Fault_1_0 |  | -
2029 | UNT_Fault_1_20 |  | -
2030 | UNT_Fault_1_40 |  | -
2031 | UNT_Fault_1_80 |  | -
2032 | UNT_Voltage-support |  | Test of reactive fault current contribution, match required static
2033 | UNT_Fault_1_restrike |  | Test of robustness for consecutive faults - single fase with auto reclosure. 2 different faults each with double strike.
2034 | UNT_Fault_3_double |  | Test of robustness for consecutive faults - 3 phase fault, 2 individual faults in a row
2035 | UNT_Fault_2_double |  | Test of robustness for consecutive faults - 2 phase fault, 2 individual faults in a row
2036 | UNT_Fault_3_20_short |  | Fault simulation with short duration, (just to have case with initially better zoom to inspect)
2037 | UNT_Fault_2_20_short |  | Fault simulation with short duration, (just to have case with initially better zoom to inspect)
2038 | UNT_Fault_3_20_WG |  | Fault simulation, test plant stability in weak grid outside required compliance. Always SCR = 2
2039 | UNT_Fault_2_20_WG |  | Fault simulation, test plant stability in weak grid outside required compliance. Always SCR = 2
2040 | UNT_Fault_3_SCR |  | Test of stability, 3 fase fault with impedance change at fault clearing. (jump from SC "tune" to SC min)
2041 | UNT_Fault_2_SCR |  | Test of stability, 2 fase fault with impedance change at fault clearing. (jump from SC "tune" to SC min)
2042 | UNT_Fault_rec_1_Q |  | Recording of fault with very slow voltage recovery. (recording from system model simulation).
2043 | UNT_Fault_rec_3_Q |  | Fault simulations with the HV transformer grounded. Test of robustness and stability.
2044 | UNT_Fault_3_SCR_freqStep |  | 3phase fault, impedance change and frequency steps. Plant stability and model robustness
2045 | Unit_SCR_step_Max-Min |  | Plant stability / model robustness - grid impedance change from Max to Min SC.
2046 | UNT_FRTsensitivity |  | Screening what happens just around FRT threshold - any toggling ? (Step)
2047 | UNT_FRTsensitivity-ramp |  | Screening what happens just around FRT threshold - any toggling ? (Ramp)
2048 | UNT_MaxPhaseJump | Robustness test / model performance | Test plant is compliant with 20deg phase jumps (large jumps)
2049 | UNT_MaxPhaseJump2 |  | Test of phasejump robustness with several consecutive smaller phasejumps adding up to 20deg over 3 periods
2050 | UNT_MaxRoCoF1 |  | Test of robusstness for RoCoF (RoCoF of either 2Hz/s or 0.5Hz/s for long time)
2051 | UNT_MaxRoCoF2 |  | Test of robusstness for RoCoF (RoCoF of either 4Hz/s for just 100ms or 20Hz/s for 20ms.)
2052 | UNT_MaxRoCoF_CurveOF |  | Test of Rocof robustness (more realistic frequency event curve with varying RoCof - over frequency
2053 | UNT_MaxRoCoF_CurveUF |  | Test of Rocof robustness (more realistic frequency event curve with varying RoCof - under frequency
2054 | UNT_MaxPhaseJump_Extreme_min |  | Test of phase jump robustness, going beyond 20deg (just screening of plant capability) 30deg and 40 deg. (also model robustness). Extreme phasejumps with increasing deg. Purpose to provoke large transient current spike. Testing both Protection functionality and model robustness. (min SC level)
2055 | UNT_MaxPhaseJump_Extreme_max |  | -
2056 | UNT_Overvoltage_characteristic | Test of protection functionality in model | Testing different overvoltage levels, when will plant trip
2057 | UNT_Undervoltage_characteristic |  | Testing different undervoltage levels, when will plant trip
2058 | UNT_VoltageRise_1.2 |  | Testing different overvoltage levels, when will plant trip
2059 | UNT_VoltageRise_1.3 |  | -
2060 | UNT_VoltageRise_1.4 |  | -
2061 | UNT_VoltageRise_1.5 |  | -
2062 | UNT_VoltageRise_insta_min |  | test with transient overvoltage spikes with increasing magnitude. (does model contain any instantinous protection? Mainly EMT model). Testing with minimum SC
2063 | UNT_VoltageRise_insta_max |  | test with transient overvoltage spikes with increasing magnitude. (does model contain any instantinous protection? Mainly EMT model). Testing with maximum SC
2064 | UNT_VoltageDip_insta_min |  | test with transient undervoltage spikes with increasing magnitude. (does model contain any instantinous protection? Mainly EMT model). Testing with minimum SC
2065 | UNT_VoltageDip_insta_max |  | test with transient undervoltage spikes with increasing magnitude. (does model contain any instantinous protection? Mainly EMT model). Testing with maximum SC
2066 | Unit_freqRise_insta_min |  | test with transient over-frequency spikes with increasing magnitude. (does model contain any instantinous protection? Mainly EMT model).
2067 | Unit_freqDip_insta_min |  | test with transient under-frequency spikes with increasing magnitude. (does model contain any instantinous protection? Mainly EMT model).
2068 | UNT_prot_Fault_3_0.8pu |  | Test with fault lasting 60seconds, when will plant trip
2069 | UNT_prot_Fault_3_0.6pu |  | -
2070 | UNT_prot_Fault_3_0.40pu |  | -
2071 | UNT_prot_Fault_3_0.20pu |  | -
2072 | UNT_prot_Fault_1_0.05pu |  | -
2073 | UNT_Freq_53Hz |  | Test with frequency just above limit, will plant trip ?
2074 | UNT_Freq_46Hz |  | Test with frequency just below limit, will plant trip ?
2075 | UNT_Freq_limit_up |  | Test with frequency increasing in steps, when will plant trip ? (does model seem to include all protection functions)
2076 | UNT_Freq_limi_down |  | Test with frequency decreasing in steps, when will plant trip ? (does model seem to include all protection functions)
2077 | UNT_Pavail_variation | Variation of available power | Can model handle variation in active power ?

## Co-located cases overview
Rank | Name | Category | Comment
|  | General information | For co-located facilities, there are virtually unlimited combinations of facility types and sizes. Therefore, the Co-located Cases tab and Co-located Cases Overview tab does not provide specific cases accompanied by detailed description of each individual test, similar to the RfG or DCC cases. Instead, the sheet focuses on high-level descriptions of the required tests. Based upon the unlimited combinations of facility types and sizes and the assumption that that the developer will have deep insight into how the facility is to be operated - which needs to be considered in the model and compliance validation - the developer is expected to setup cases relevant for the specific facility to utilize the MTB for the purpose of co-located facilities. Below is a description of the types of tests which is generally performed to showcase compliance, detaling the reasoning for the tests as well as relevant considerations. Please note: This sheet is not intended as the only solution for showcasing facility compliance or validation, but rather as a preliminary guideline focused on describing the different types of tests generally performed to showcase compliance.
|  | Steady state - model performance/convergence | It is essential that the simulation models are able to initialize correctly and achieve a flat run within the required deviation/timeframe (RMS: dx/dt < 0.0001; EMT: within 3 seconds). For co-located facilities, different operating scenarios (e.g. initial voltage, active and reactive power) and control strategies (voltage control, constant Q control, or power factor control) should be be considered. Asymmetrical production + energy storage: • Consider the asymmetrical production unit under different operating scenarios and control strategies. • Consider the energy storage unit under different operating scenarios and control strategies. Both production and consumption modes should be assessed. • In a co-located facility, it is equally important to verify correct initialization of each individual unit and of the full facility. Both cases should therefore be included in the steady-state tests. Asymmetrical production + energy storage + demand: • Consider the asymmetrical production unit under different operating scenarios and control strategies. • Consider the energy storage unit under different operating scenarios and control strategies, including both production and consumption modes. • Consider the demand unit under different operating scenarios. When assessed as a standalone unit, particular attention should be given to reactive power requirements. • As for other co-located configurations, both individual unit initialization and full facility initialization should be validated.
|  | Reactive power capability + Reactive power in full voltage range | The co-located facility must comply with both U/Q and P/Q requirements. The full operating area should be assessed, and different operating configurations (e.g. limited asymmetrical production or limited battery charge) should be investigated. Asymmetrical production + energy storage: • Consider the asymmetrical production unit. P/Q compliance scenarios with limited available power should be investigated. • Consider the energy storage unit in both production and consumption modes. P/Q compliance scenarios with limited stored energy should be included. • In a co-located facility, the requirements and capabilities of each unit should be assessed individually as well as in coordinated operation. Asymmetrical production + energy storage + demand: • Consider the asymmetrical production unit. P/Q compliance scenarios with limited available power should be investigated. • Consider the energy storage unit in both production and consumption modes. P/Q compliance scenarios with limited stored energy should be included. • Consider the demand unit. Depending on the demand technology, the requirements should at least be validated for different initial operating conditions (e.g. initial voltage and active power). Where technically feasible, active power setpoint changes should also be included to validate the power factor. • In a co-located facility, the requirements and capabilities of each unit should be assessed individually as well as in coordinated operation.
|  | Voltage control, Q-mode and Pf-mode regulation | The co-located facility must comply with the applicable reactive power control requirements. • Q mode: Different initial setpoints should be considered. Setpoint changes across the full range (±0.33 p.u. of PnG3) should be validated. • Voltage control: Different initial voltage references should be tested. Voltage disturbances of varying magnitude should be applied to demonstrate controller sensitivity. Different system strengths should be considered to validate rise time and overshoot, with overshoot limited to 20% at SCRmin. • PF mode: Different initial power factor references should be considered. The facility should correctly distinguish between inductive and capacitive power factor operation (e.g. −0.95 vs. +0.95). For both asymmetrical production + energy storage and asymmetrical production + energy storage + demand, the facility must comply with the reactive power requirements under all relevant operating conditions. If one unit is out of service or limited by available or stored energy, the remaining units must continue reactive power regulation where technically possible. For example, if reactive power regulation is shared between asymmetrical production and energy storage and one unit is unavailable, the remaining unit must provide the full reactive power response (if technically possible). Each unit could therefore also be assessed individually.
|  | Active Power Setpoint Changes | The co-located facility must comply with the active power ramp-rate requirements (20% of PnG3 or PnD3 per minute, limited to a maximum of 60 MW/min). Asymmetrical production + energy storage: • Consider the asymmetrical production unit. • Consider the energy storage unit in both production and consumption modes. • Scenarios in which both units receive simultaneous setpoint changes should be investigated. Compliance with ramp-rate requirements must be validated at the POC. Asymmetrical production + energy storage + demand: • Consider the asymmetrical production unit. • Consider the energy storage unit in both production and consumption modes. • Consider the demand unit. Where technically feasible, active power setpoint changes should be included (project-specific assessment). • Scenarios with simultaneous setpoint changes of all units should be validated at the POC.
|  | Limited available energy or charge | The simulation model must accurately represent the physical facility. Scenarios with reduced or increased available energy (e.g. due to irradiance or wind speed variations) must be included. Relevant communication between asymmetrical production units and plant control must be represented accurately. Different energy storage states of charge should be considered, including validation of: • Consumption capability at full charge • Production capability at zero charge
|  | Frequency (FSM, LFSM and LFDD) | The co-located facility must include all relevant frequency response functions. Asymmetrical production + energy storage • Consider both units, including production and consumption modes for energy storage. • Verify that each unit can provide FSM and LFSM functionality both individually and as part of the coordinated facility response. • Include scenarios that may challenge PnG3 or PnD3 at the POC to validate plant control performance. Asymmetrical production + energy storage + demand • If a demand unit is included, LFDD requirements apply and must be coordinated with asymmetrical production and energy storage. PnG3 and PnD3 limits must not be exceeded. • If the demand unit is subject to LFSM U requirements, this functionality must be included in the coordinated response. • Include scenarios that may challenge PnG3 or PnD3 at the POC to validate plant control performance.
|  | Systemguard (SIPS) | The co-located facility must implement system guard functionality to limit generation or consumption based on PnG3 and PnD3. The system guard signal depends on the operational state (generation or consumption). Asymmetrical production + energy storage: • Consider both units, including production and consumption modes for energy storage. • Validate coordinated responses for generation, consumption, and balanced operation (generation ≈ consumption). Asymmetrical production + energy storage + demand: • Consider all units, including production and consumption modes for energy storage. • Validate coordinated responses for generation, consumption, and balanced operation (generation ≈ consumption).
|  | Manual disconnection (Manal aflastning) | Energy storage and demand units must include manual disconnection functionality to represent the actual facility. For energy storage, the operational mode (generation or consumption) determines the applicable response. The coordinated facility response must be validated to ensure that PnG3 limits are not exceeded.
|  | Facility robustness (RoCoF and Phase jumps) | The facility must withstand specified RoCoF and phase jump events. Validation should include a range of RoCoF and phase jump scenarios. Where possible, extreme events should also be tested to determine the trip thresholds of the facility.
|  | Overvoltage, undervoltage, short circuit, reactive fault current and PFAPR | The co-located facility must be robust against over- and undervoltage events, provide reactive fault current (scaled by PnG3), and restore active power in POC to pre-fault levels, even if energy storage and/or demand units disconnect. • Validate OVRT and LVRT performance using the required profiles. • If a demand unit is present, consider for differences between generation and consumption LVRT profiles. If the demand unit disconnects, the asymmetrical production must restore the active power in POC to pre-fault levels. The coordinated facility response must be assessed. PFAPR performance must be validated for generation, consumption, and balanced (generation ≈ consumption) operating conditions. The required response depends on the pre-fault operating state. During LVRT or short-circuit events (3-phase, 2-phase and 1-phase), additional reactive fault current must be provided based on PnG3. Both individual-unit and combined facility responses must be considered. For validation of plant control freeze behaviour, consider fault scenarios combined with a systemguard event at fault clearing. Similar validation could be performed with the facility operating in voltage control mode. Different initial setpoints and available power levels should also be considered to ensure a representative and compliant response.
|  | Test of protection functionality in model | To validate protection implementation at unit and facility level, include tests with long-duration high and low frequency and voltage conditions. Additionally, include single-phase fault scenarios with the main transformer grounded on the HV side.

## Custom cases overview
Rank | Name | Category | Comment
4001 | Custom_RfG_MaxFacilityCurrent | Max Facility Current | Lower operation voltage, 1 p.u. active power reference and 0.33 p.u. reactive power reference. Test of maximum facility current.
4002 | Custom_RfG_Fault_3_FRTtrig_0.87pu | Trigger FRT - Sensitivity | -
4003 | Custom_RfG_Fault_3_FRTtrig_0.86pu |  | -
4004 | Custom_RfG_Fault_3_FRTtrig_0.85pu |  | Test of FRT triggering voltage. 3-phase faults, with different residual voltages, will show when the facility enters FRT and could be validated at inverter/tubine/... terminals when considering the reactive fault current. (Change the green cell and all cases/names in this section will update. As standard these value will change based on the Settings.)
4005 | Custom_RfG_Fault_3_FRTtrig_0.84pu |  | -
4006 | Custom_RfG_Fault_3_FRTtrig_0.83pu |  | -
4007 | Custom_RfG_Fault_3_FRTtrig_0.82pu |  | -
4008 | Custom_RfG_Fault_3_FRTtrig_0.81pu |  | -
4009 | Custom_RfG_Fault_3_FRTtrig_0.80pu |  | -
4010 | Custom_RfG_Fault_3_FRTtrig_0.79pu |  | -
4011 | Custom_RfG_Fault_3_FRTtrig_0.78pu |  | -
4012 | Custom_RfG_LVRT_FRTexit_0.84pu | Exit FRT - Sensitivity | -
4013 | Custom_RfG_LVRT_FRTexit_0.85pu |  | Test of FRT exit voltage. The LVRT curve is modified with different voltage levels to validate when the facility exits FRT. (Change the green cell and all cases/names in this section will update. As standard these value will change based on the Settings.)
4014 | Custom_RfG_LVRT_FRTexit_0.86pu |  | -
4015 | Custom_RfG_LVRT_FRTexit_0.87pu |  | -
4016 | Custom_RfG_LVRT_FRTexit_0.88pu |  | -
4017 | Custom_RfG_LVRT_FRTexit_0.89pu |  | -
4018 | Custom_RfG_Fault_3_MaxIQ_0.24pu | Reactive Fault Current Toggeling - Sensitivity | -
4019 | Custom_RfG_Fault_3_MaxIQ_0.23pu |  | -
4020 | Custom_RfG_Fault_3_MaxIQ_0.22pu |  | -
4021 | Custom_RfG_Fault_3_MaxIQ_0.21pu |  | -
4022 | Custom_RfG_Fault_3_MaxIQ_0.20pu |  | Test of toggling reactive fault current. Energinet have experienced that control in dynamic power electronic elements can causes toggling between “full” and “partial” reactive fault current during fault, which can cause oscillations in active power, reactive power and voltage. In some cases, this has triggered facility protection. This test is to ensure robustness and stability. The sensitivity will depend on K-factor and SCR. (Change the green cell and all cases/names in this section will update. This parameter must be changed to the specific facility.)
4023 | Custom_RfG_Fault_3_MaxIQ_0.19pu |  | -
4024 | Custom_RfG_Fault_3_MaxIQ_0.18pu |  | -
4025 | Custom_RfG_Fault_3_MaxIQ_0.17pu |  | -
4026 | Custom_RfG_Fault_3_MaxIQ_0.16pu |  | -
4027 | Custom_RfG_Fault_3_MaxIQ_0.15pu |  | -
4028 | Custom_RfG_Fault_3_0.2pu_Plim_0.5pu | Fault and Limited Available Power | Fault simulations with the "default" Q-mode and available power of 0.50 p.u.. The facility must ensure correct behavior during lower available power.
4029 | Custom_RfG_Fault_2_0.2pu_Plim_0.5pu |  | -
4030 | Custom_RfG_Fault_1_0.2pu_Plim_0.5pu |  | -
4031 | Custom_RfG_Fault_3_0.2pu_Plim_0.15pu |  | Fault simulations with the "default" Q-mode and available power of 0.15 p.u.. The facility must ensure correct behavior during lower available power.
4032 | Custom_RfG_Fault_2_0.2pu_Plim_0.15pu |  | -
4033 | Custom_RfG_Fault_1_0.2pu_Plim_0.15pu |  | -
4034 | Custom_RfG_Ucontrol_Plim_1.00pu | U-Mode and Limited Available Power | Test of voltage control with limited available power of 1.0 p.u.. The facility must ensure correct behavior during lower available power.
4035 | Custom_RfG_Ucontrol_Plim_0.50pu |  | Test of voltage control with limited available power of 0.5 p.u.. The facility must ensure correct behavior during lower available power.
4036 | Custom_RfG_Ucontrol_Plim_0.15pu |  | Test of voltage control with limited available power of 0.15 p.u.. The facility must ensure correct behavior during lower available power.
4037 | Custom_Fault_3_0.20pu_U0_1.118pu | Fault from Upper/Lower Continuous Voltage | Fault simulations with “default” Q-mode. Operating voltage equal to upper continuous voltage. Test of reactive-fault current, robustness and stability.
4038 | Custom_Fault_2_0.20pu_U0_1.118pu |  | -
4039 | Custom_Fault_1_0.20pu_U0_1.118pu |  | -
4040 | Custom_Fault_3_0.20pu_U0_0.968pu |  | Fault simulations with “default” Q-mode. Operating voltage equal to lower continuous voltage. Test of reactive-fault current, robustness and stability.
4041 | Custom_Fault_2_0.20pu_U0_0.968pu |  | -
4042 | Custom_Fault_1_0.20pu_U0_0.968pu |  | -
4043 | Custom_Fault_3_U0_1.118_Uend_1.065 | Fault and Increased/Reduced Voltage Post-Fault | Fault simulations with “default” Q-mode. Operating voltage equal to upper continuous voltage and is reduced after fault. Test of reactive-fault current, robustness and stability.
4044 | Custom_Fault_2_U0_1.118_Uend_1.065 |  | -
4045 | Custom_Fault_1_U0_1.118_Uend_1.065 |  | -
4046 | Custom_Fault_3_U0_1.118_Uend_0.968 |  | -
4047 | Custom_Fault_3_U0_0.959_Uend_1.065 |  | Fault simulations with “default” Q-mode. Operating voltage equal to upper continuous voltage and is increased after fault. Test of reactive-fault current, robustness and stability.
4048 | Custom_Fault_2_U0_0.959_Uend_1.065 |  | -
4049 | Custom_Fault_1_U0_0.959_Uend_1.065 |  | -
4050 | Custom_Fault_3_U0_0.959_Uend_1.118 |  | -
4051 | Custom_Fault_3_U0_1.118_Uend_0.900 |  | Fault simulations with “default” Q-mode. Operating voltage equal to upper continuous voltage and is reduced after fault. Test of reactive-fault current, PFAPR, robustness and stability.
4052 | Custom_Fault_3_U0_1.065_Uend_0.900 |  | -
4053 | Custom_Fault_3_U0_0.959_Uend_0.900 |  | -
4054 | Custom_Fault_3_U0_1.065pu_OVRT_1.15 | Fault and Transition into HVRT | Fault simulation with Q-mode and transition into reduced HVRT. Test of facility behavior, reactive fault current robustness and stability.
4055 | Custom_Fault_3_U0_1.065pu_OVRT_1.20 |  | Fault simulation with Q-mode and transition into reduced HVRT. Test of facility behavior, reactive fault current robustness and stability.
4056 | Custom_Fault_3_U0_1.065pu_OVRT_1.30 |  | Fault simulation with Q-mode and transition into full HVRT (standard profile). Test of facility behavior, reactive fault current robustness and stability.
4057 | Custom_Fault_3_U0_1.065pu_OVRT_1.15 |  | Fault simulation with U-mode and transition into reduced HVRT. Test of facility behavior, reactive fault current robustness and stability.
4058 | Custom_Fault_3_U0_1.065pu_OVRT_1.20 |  | Fault simulation with U-mode and transition into reduced HVRT. Test of facility behavior, reactive fault current robustness and stability.
4059 | Custom_Fault_3_U0_1.065pu_OVRT_1.30 |  | Fault simulation with U-mode and transition into full HVRT (standard profile). Test of facility behavior, reactive fault current robustness and stability.
4060 | Custom_Fault_3_0.20pu_SCR_2 | Fault Stability in Weak Grid - Sensitivity | Fault simulation, test plant stability and sensitivity in stepwise weak grid.
4061 | Custom_Fault_3_0.20pu_SCR_3 |  | -
4062 | Custom_Fault_3_0.20pu_SCR_4 |  | -
4063 | Custom_Fault_3_0.20pu_SCR_5 |  | -
4064 | Custom_Fault_3_0.20pu_SCR_6 |  | -
4065 | Custom_Fault_2_0.20pu_SCR_2 |  | -
4066 | Custom_Fault_2_0.20pu_SCR_3 |  | -
4067 | Custom_Fault_2_0.20pu_SCR_4 |  | -
4068 | Custom_Fault_2_0.20pu_SCR_5 |  | -
4069 | Custom_Fault_2_0.20pu_SCR_6 |  | -
4070 | Custom_Fault_3_0.70pu_SCR_2 |  | -
4071 | Custom_Fault_3_0.70pu_SCR_3 |  | -
4072 | Custom_Fault_3_0.70pu_SCR_4 |  | -
4073 | Custom_Fault_3_0.70pu_SCR_5 |  | -
4074 | Custom_Fault_3_0.70pu_SCR_6 |  | -
4075 | Custom_Fault_2_0.70pu_SCR_2 |  | -
4076 | Custom_Fault_2_0.70pu_SCR_3 |  | -
4077 | Custom_Fault_2_0.70pu_SCR_4 |  | -
4078 | Custom_Fault_2_0.70pu_SCR_5 |  | -
4079 | Custom_Fault_2_0.70pu_SCR_6 |  | -
4080 | Custom_Fault_3_0.20pu_Duration_80 | Fault Duration or Shift | Fast fault simulations with the "default" Q-mode. The duration is lower and not a product of 100ms or equal to assumed PPC sampling time.
4081 | Custom_Fault_3_0.20pu_Duration_60 |  | -
4082 | Custom_Fault_3_0.20pu_Duration_40 |  | -
4083 | Custom_Shift_10_Fault_3_0.20pu |  | Fast fault simulations with the "default" Q-mode. The fault is shifted in time and duration is lower and not a product of 100ms or equal to assumed PPC sampling time.
4084 | Custom_Shift_20_Fault_3_0.20pu |  | -
4085 | Custom_Shift_30_Fault_3_0.20pu |  | -
4086 | Custom_Shift_40_Fault_3_0.20pu |  | -
4087 | Custom_Shift_50_Fault_3_0.20pu |  | -

## datavalidation (hidden)
DK1 | Q | No P(f) | Max | TRUE | RfG
DK2 | Q(U) | LFSM | Min | FALSE | DCC
| PF | FSM | Tuning |  | Unit
| Default | LFSM+FSM | Ideal |  | Custom
| Qmode3 | Pmode4
| Qmode4 | Pmode5
| Qmode5 | Pmode6
| Qmode6 | Pmode7